## Summary
CDU Factory Test Report
Work Order Number
Sale Order Number
Part Number
Software Version
Firmware Version
Serial Number
Tested by
Date Tested
Final Result
Active Alarms Test
Active Alarms

## Measurements
Time | Status` | Group | TT01 | TT02 | TT31 | TT41 | PT01 | PT02 | PT31 | PT41 | PT32 | PT42 | PT21 | PT11 | TT01/TT02 | TT31/TT41 | PT01/PT02 | PT32/PT41 | Pump 31 Filter DP | Pump 41 Filter DP | DP (Supply - Return) | FL 01 | P31 Speed | P41 Speed | Fan 1 Speed | Fan 2 Speed | Fan 3 Speed | Fan 4 Speed | Air Humidity | Air Temperature | Program version | Secondary Temperature Setpoint | Secondary DP Setpoint | Secondary Flow Setpoint
sec | [] | [] | F | F | F | F | PSI | PSI | PSI | PSI | PSI | PSI | PSI | PSI | F | F | PSI | PSI | PSI | PSI | PSI | lpm | lpm | % | % | % | % | % | % | F | [] | F | PSI | lpm
12 | 0 | 0 | 71.1 | 70.9 | 70.9 | 71 | 27.5 | 27.3 | 29 | 28.9 | 27.4 | 27.5 | 30.2 | 0.7 | 71 | 70.9 | 27.4 | 27.4 | 1.6 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9 | 69.2 | 21.9 | 40 | 30 | 30

## Description of Diagnostics
Fault Code | Description of the Diagnostic | Purpose of the Diagnostic | Troubleshooting Guide
Fault Code 1 : Abnormal High Primary Flow Check | Primary flow is compared to the upper limit for uncertainty*secondary flow. If primary flow is greater than the result, then the diagnostic is a fail | Primary flow shouldn't be higher than upper limit for uncertainty*(secondary flow). Primary flow should be equal to secondary flow. | Either the primary flow is too high. Or the secondary flow is too low. One of the two sensors is not working properly.
Fault Code 2 : Abnormal Low Primary Flow Check | Primary flow is compared to the lower limit for uncertainty*secondary flow. If primary flow is smaller than the result, then the diagnostic is a fail | Primary flow shouldn't be lower than lower limit for uncertainty*(secondary flow). Primary flow should be equal to secondary flow. | Either the primary flow is too low. Or the secondary flow is too high. One of the two sensors is not working properly.
Fault Code 3 : Abnormal High Secondary Flow Check | If the secondary flow is higher than the upper limit for uncertainty* the nominal secondary flow from PQ cureve, then the diagnostic is a fail. | The secondary flow at 100% of all the pumps should be close to the PQ curve of the golden unit. | Either the pumps are providng excessive flow or the secondary flow sensor is not working properly. Check fault codes 1
Fault Code 4 : Abnormal Low Secondary Flow Check | If the secondary flow is lower than the lower limit for uncertainty* the nominal secondary flow from PQ cureve, then the diagnostic is a fail. | The secondary flow at 100% of all the pumps should be close to the PQ curve of the golden unit. | Either the pumps are providng low flow or the the secondary flow sensor is not working properly.
Fault Code 5: Abnormal High Secondary Differential Pressure Check | If the secodary differential pressure is higher than the upper limit for uncertainty*[X-loop differential pressure], then the diagnostic is a fail. | The secondary differential pressure should be close to the X-loop expected differential pressure. | The secondary pressure sensors are likely not working properly.
Fault Code 6: Abnormal Low Secondary Differential Pressure Check | If the secodary differential pressure is lower than the lower limit for uncertainty*[X-loop differential pressure], then the diagnostic is a fail. | The secondary differential pressure should be close to the X-loop expected differential pressure. | The secondary pressure sensors are likely not working properly.
Fault Code 7: Abnormal High Primary Supply Temperature Check | If the primary supply temperature is higher than the upper limit for uncertainty*Average of (primary return temperature, secondary supply temperature, secondary return temperature), then the diagnostic is a fail. | The four temperature sensors (primary supply, primary return, secondary supply secondary return) should have very similar temperature. | Check primary supply temperature wiring and sensor.
Fault Code 8: Abnormal Low Primary Supply Temperature Check | If the primary supply temperature is lower than the lower limit for uncertainty*Average of (primary return temperature, secondary supply temperature, secondary return temperature), then the diagnostic is a fail. | The four temperature sensors (primary supply, primary return, secondary supply secondary return) should have very similar temperature. | Check primary supply temperature wiring and sensor.
Fault Code 9: Abnormal High Secondary Supply Temperature Check | If the secondary supply temperature is higher than the upper limit for uncertainty*Average of (primary return temperature, primary supply temperature, secondary return temperature), then the diagnostic is a fail. | The four temperature sensors (primary supply, primary return, secondary supply secondary return) should have very similar temperature. | Check secondary supply temperature wiring and sensor.
Fault Code 10: Abnormal Low Secondary Supply Temperature Check | If the secondary supply temperature is lower than the lower limit for uncertainty*Average of (primary return temperature, primary supply temperature, secondary return temperature), then the diagnostic is a fail. | The four temperature sensors (primary supply, primary return, secondary supply secondary return) should have very similar temperature. | Check secondary supply temperature wiring and sensor.
Fault Code 11: Abnormal High Primary Return Temperature Check | If the primary return temperature is higher than the upper limit for uncertainty*Average of (primary supply temperature, secondary supply temperature, secondary return temperature), then the diagnostic is a fail. | The four temperature sensors (primary supply, primary return, secondary supply secondary return) should have very similar temperature. | Check primary return temperature wiring and sensor.
Fault Code 12: Abnormal Low Primary Return Temperature Check | If the primary return temperature is lower than the lower limit for uncertainty*Average of (primary supply temperature, secondary supply temperature, secondary return temperature), then the diagnostic is a fail. | The four temperature sensors (primary supply, primary return, secondary supply secondary return) should have very similar temperature. | Check primary return temperature wiring and sensor.
Fault Code 13: Abnormal High Secondary Return Temperature Check | If the secondary temperature is higher than the upper limit for uncertainty*Average of (primary return temperature, primary supply temperature, secondary supply temperature), then the diagnostic is a fail. | The four temperature sensors (primary supply, primary return, secondary supply secondary return) should have very similar temperature. | Check secondary return temperature wiring and sensor.
Fault Code 14: Abnormal Low Secondary Return Temperature Check | If the secondary temperature is lower than the lower limit for uncertainty*Average of (primary return temperature, primary supply temperature, secondary supply temperature), then the diagnostic is a fail. | The four temperature sensors (primary supply, primary return, secondary supply secondary return) should have very similar temperature. | Check secondary return temperature wiring and sensor.
Fault Code 15: Abnormal High Pump 0 Speed | If pump 0 speed is higher than the upper limit for pump speed, then the diagnostic is a fail. | Pump speed for all the pumps should be within lower and upper limit. | Chech the SW/FW revision. Check pump 0 and its wiring.
Fault Code 16: Abnormal Low Pump 0 Speed | If pump 0 speed is lower than the lower limit for pump speed, then the diagnostic is a fail. | Pump speed for all the pumps should be within lower and upper limit. | Chech the SW/FW revision. Check pump 0 and its wiring.
Fault Code 17: Abnormal High Pump 1 Speed | If pump 1 speed is higher than the upper limit for pump speed, then the diagnostic is a fail. | Pump speed for all the pumps should be within lower and upper limit. | Chech the SW/FW revision. Check pump 1 and its wiring.
Fault Code 18: Abnormal Low Pump 1 Speed | If pump 1 speed is lower than the lower limit for pump speed, then the diagnostic is a fail. | Pump speed for all the pumps should be within lower and upper limit. | Chech the SW/FW revision. Check pump 1 and its wiring.
Fault Code 19: Abnormal High Pump 2 Speed | If pump 2 speed is higher than the upper limit for pump speed, then the diagnostic is a fail. | Pump speed for all the pumps should be within lower and upper limit. | Chech the SW/FW revision. Check pump 2 and its wiring.
Fault Code 20: Abnormal Low Pump 2 Speed | If pump 2 speed is lower than the lower limit for pump speed, then the diagnostic is a fail. | Pump speed for all the pumps should be within lower and upper limit. | Chech the SW/FW revision. Check pump 2 and its wiring.