## Summary
CDU Factory Test Report
Work Order Number | WO2602286
Sale Order Number | SO
Part Number | 900-02233
Software Version | 0.23
Firmware Version | 1.41.329
Serial Number | CD050L
Tested by | mdtahmid.jami
Date Tested | 2026-10-01
Final Result | Fail
Active Alarms Test
Active Alarms

## Measurements
Time | Status (0-off 1-on) | Group (0-standalone 1-Group lead 2-Group follow) | TT01 | TT02 | TT31 | TT41 | TT61 | TT62 | TT51 | TT52 | TT45 | PT01 | PT02 | PT31 | PT41 | PT32 | PT42 | PT21 | PT11 | PT51 | PT52 | PT53 | PT61 | PT62 | TT01/TT02 | TT31/TT41 | TT61/TT62 | TT51/TT52 | PT01/PT02 | PT32/PT42 | PT61/PT62 | PT51/PT52 | Pump 31 Filter DP | Pump 41 Filter DP | Primary Filter 53 DP | Secondary DP (Supply - Return) | Primary DP (Supply - Return) | FT01 | FT61 | P31 Speed % | P41 Speed % | FCV61 Actual Flow% | FCV61 Actual Open% | Air Humidity | Air Temperature | Program version | Secondary Temperature Setpoint | Secondary DP Setpoint | Secondary Flow Setpoint
sec | [] | [] | C | C | C | C | PSI | PSI | PSI | PSI | PSI | PSI | PSI | PSI | C | C | PSI | PSI | PSI | PSI | PSI | g/min | % | % | % | % | % | % | % | C | [] | C | PSI | g/min | PSI | PSI | PSI | FT | FT | % | % | % | % | % | C | [] | C | PSI | g/m
15 | 1 | 0 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.3 | 27.4 | 26.4 | 29.2 | 29.3 | 44.6 | 44.7 | 42.7 | 42.5 | 22.9 | 6553.5 | 33.7 | 33.7 | 33.1 | 42.2 | 42.5 | 27.4 | 27.4 | 27.4 | 27.3 | 29.2 | 42.6 | 42.4 | 33.7 | 44.7 | 2.1 | 0.6 | 15.9 | 6544.9 | 1579.8 | 1157.2 | 6 | 6 | 10 | 9.9 | 20.1 | 22.1 | 23 | 40 | 15 | 100
15 | 1 | 0 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.3 | 27.4 | 26.4 | 29.2 | 29.3 | 44.6 | 44.7 | 42.7 | 42.5 | 22.9 | 6553.5 | 33.7 | 33.7 | 33.1 | 42.2 | 42.5 | 27.4 | 27.4 | 27.4 | 27.3 | 29.2 | 42.6 | 42.4 | 33.7 | 44.7 | 2.1 | 0.6 | 15.9 | 6544.9 | 1579.8 | 1157.2 | 6 | 6 | 10 | 9.9 | 20.1 | 22.1 | 23 | 21 | 15 | 100
15 | 1 | 0 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.3 | 27.4 | 26.4 | 29.2 | 29.3 | 44.6 | 44.7 | 42.7 | 42.5 | 22.9 | 6553.5 | 33.7 | 33.7 | 33.1 | 42.2 | 42.5 | 27.4 | 27.4 | 27.4 | 27.3 | 29.2 | 42.6 | 42.4 | 33.7 | 44.7 | 2.1 | 0.6 | 15.9 | 6544.9 | 1579.8 | 1157.2 | 6 | 6 | 10 | 9.9 | 20.1 | 22.1 | 23 | 21 | 5 | 100
75 | 1 | 0 | 27.6 | 27.6 | 27.6 | 27.5 | 27.5 | 27.6 | 27.5 | 27.6 | 26.6 | 29.2 | 29.2 | 42.8 | 42.8 | 41.1 | 40.9 | 23.6 | 0 | 33.3 | 33.2 | 32.6 | 40.9 | 41.1 | 27.6 | 27.6 | 27.6 | 27.5 | 29.2 | 41 | 41 | 33.3 | 42.8 | 1.8 | 0.7 | 14.3 | 6545.9 | 1336.9 | 1017.8 | 5.6 | 5.6 | 10 | 9.9 | 21 | 22.1 | 23 | 21 | 5 | 160
75 | 1 | 0 | 27.6 | 27.6 | 27.6 | 27.5 | 27.5 | 27.6 | 27.5 | 27.6 | 26.6 | 29.2 | 29.2 | 42.8 | 42.8 | 41.1 | 40.9 | 23.6 | 0 | 33.3 | 33.2 | 32.6 | 40.9 | 41.1 | 27.6 | 27.6 | 27.6 | 27.5 | 29.2 | 41 | 41 | 33.3 | 42.8 | 1.8 | 0.7 | 14.3 | 6545.9 | 1336.9 | 1017.8 | 5.6 | 5.6 | 10 | 9.9 | 21 | 22.1 | 23 | 21 | 5 | 160
75 | 1 | 0 | 27.6 | 27.6 | 27.6 | 27.5 | 27.5 | 27.6 | 27.5 | 27.6 | 26.6 | 29.2 | 29.2 | 42.8 | 42.8 | 41.1 | 40.9 | 23.6 | 0 | 33.3 | 33.2 | 32.6 | 40.9 | 41.1 | 27.6 | 27.6 | 27.6 | 27.5 | 29.2 | 41 | 41 | 33.3 | 42.8 | 1.8 | 0.7 | 14.3 | 6545.9 | 1336.9 | 1017.8 | 5.6 | 5.6 | 10 | 9.9 | 21 | 22.1 | 23 | 21 | 10 | 160
135 | 1 | 0 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 26.8 | 29.1 | 29.2 | 42.7 | 42.8 | 41.1 | 40.8 | 23.5 | 0 | 33.3 | 33.2 | 32.5 | 40.8 | 41 | 27.7 | 27.7 | 27.7 | 27.7 | 29.2 | 40.9 | 40.9 | 33.2 | 42.7 | 1.8 | 0.7 | 14.3 | 6545.9 | 1326.8 | 1020.6 | 5.6 | 5.6 | 10 | 9.9 | 21.5 | 22.1 | 23 | 21 | 10 | 320
135 | 1 | 0 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 26.8 | 29.1 | 29.2 | 42.7 | 42.8 | 41.1 | 40.8 | 23.5 | 0 | 33.3 | 33.2 | 32.5 | 40.8 | 41 | 27.7 | 27.7 | 27.7 | 27.7 | 29.2 | 40.9 | 40.9 | 33.2 | 42.7 | 1.8 | 0.7 | 14.3 | 6545.9 | 1326.8 | 1020.6 | 5.6 | 5.6 | 10 | 9.9 | 21.5 | 22.1 | 23 | 22 | 10 | 320
135 | 1 | 0 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 26.8 | 29.1 | 29.2 | 42.7 | 42.8 | 41.1 | 40.8 | 23.5 | 0 | 33.3 | 33.2 | 32.5 | 40.8 | 41 | 27.7 | 27.7 | 27.7 | 27.7 | 29.2 | 40.9 | 40.9 | 33.2 | 42.7 | 1.8 | 0.7 | 14.3 | 6545.9 | 1326.8 | 1020.6 | 5.6 | 5.6 | 10 | 9.9 | 21.5 | 22.1 | 23 | 22 | 25 | 320
195 | 1 | 0 | 28 | 27.9 | 28.1 | 27.9 | 28 | 28.1 | 27.9 | 28 | 26.9 | 29.9 | 29.9 | 54.7 | 55 | 52.3 | 52 | 20.8 | 0 | 37.2 | 37.1 | 36.5 | 50.4 | 50.6 | 27.9 | 28 | 28 | 27.9 | 29.9 | 52.1 | 50.5 | 37.2 | 54.9 | 2.7 | 0.7 | 24.8 | 6540.3 | 1811.3 | 1418.8 | 7.4 | 7.4 | 10 | 9.9 | 21.9 | 22.1 | 23 | 22 | 25 | 480
195 | 1 | 0 | 28 | 27.9 | 28.1 | 27.9 | 28 | 28.1 | 27.9 | 28 | 26.9 | 29.9 | 29.9 | 54.7 | 55 | 52.3 | 52 | 20.8 | 0 | 37.2 | 37.1 | 36.5 | 50.4 | 50.6 | 27.9 | 28 | 28 | 27.9 | 29.9 | 52.1 | 50.5 | 37.2 | 54.9 | 2.7 | 0.7 | 24.8 | 6540.3 | 1811.3 | 1418.8 | 7.4 | 7.4 | 10 | 9.9 | 21.9 | 22.1 | 23 | 23 | 25 | 480
195 | 1 | 0 | 28 | 27.9 | 28.1 | 27.9 | 28 | 28.1 | 27.9 | 28 | 26.9 | 29.9 | 29.9 | 54.7 | 55 | 52.3 | 52 | 20.8 | 0 | 37.2 | 37.1 | 36.5 | 50.4 | 50.6 | 27.9 | 28 | 28 | 27.9 | 29.9 | 52.1 | 50.5 | 37.2 | 54.9 | 2.7 | 0.7 | 24.8 | 6540.3 | 1811.3 | 1418.8 | 7.4 | 7.4 | 10 | 9.9 | 21.9 | 22.1 | 23 | 23 | 33 | 480
255 | 1 | 0 | 28.5 | 28.4 | 28.6 | 28.5 | 28.5 | 28.6 | 28.4 | 28.5 | 27.2 | 31 | 31 | 64.3 | 64.6 | 61.3 | 61.1 | 19.1 | 0 | 40.9 | 40.8 | 40.2 | 58.2 | 58.5 | 28.4 | 28.5 | 28.5 | 28.4 | 31 | 61.2 | 58.3 | 40.8 | 64.5 | 3.2 | 0.6 | 32.8 | 6536.1 | 2100.2 | 1656 | 8.6 | 8.6 | 10 | 9.9 | 22.2 | 22 | 23 | 23 | 33 | 560
255 | 1 | 0 | 28.5 | 28.5 | 28.6 | 28.5 | 28.5 | 28.6 | 28.4 | 28.5 | 27.3 | 30.9 | 31 | 64.5 | 64.9 | 61.6 | 61.1 | 19.1 | 0 | 40.9 | 40.8 | 40.2 | 58.1 | 58.4 | 28.5 | 28.5 | 28.5 | 28.4 | 31 | 61.3 | 58.3 | 40.9 | 64.7 | 3.4 | 0.7 | 32.8 | 6536.2 | 2103.1 | 1657.4 | 8.6 | 8.6 | 10 | 9.9 | 22.2 | 22 | 23 | 23 | 33 | 560
255 | 1 | 0 | 28.5 | 28.5 | 28.6 | 28.5 | 28.5 | 28.6 | 28.4 | 28.5 | 27.3 | 30.9 | 31 | 64.5 | 64.9 | 61.6 | 61.1 | 19.1 | 0 | 40.9 | 40.8 | 40.2 | 58.1 | 58.4 | 28.5 | 28.5 | 28.5 | 28.4 | 31 | 61.3 | 58.3 | 40.9 | 64.7 | 3.4 | 0.7 | 32.8 | 6536.2 | 2103.1 | 1657.4 | 8.6 | 8.6 | 10 | 9.9 | 22.2 | 22 | 23 | 23 | 15 | 560
315 | 1 | 0 | 28.8 | 28.7 | 28.8 | 28.7 | 28.7 | 28.8 | 28.7 | 28.8 | 27.5 | 29.4 | 29.5 | 44.4 | 44.5 | 42.7 | 42.5 | 23.2 | 6553.5 | 34 | 33.9 | 33.3 | 42.3 | 42.5 | 28.7 | 28.7 | 28.7 | 28.7 | 29.4 | 42.6 | 42.4 | 33.9 | 44.5 | 1.9 | 0.6 | 15.6 | 6545.1 | 1434.6 | 1101.1 | 5.9 | 5.9 | 10 | 9.9 | 22.2 | 22 | 23 | 23 | 15 | 380
315 | 1 | 0 | 28.8 | 28.7 | 28.8 | 28.7 | 28.7 | 28.8 | 28.7 | 28.8 | 27.5 | 29.4 | 29.5 | 44.4 | 44.5 | 42.7 | 42.5 | 23.2 | 6553.5 | 34 | 33.9 | 33.3 | 42.3 | 42.5 | 28.7 | 28.7 | 28.7 | 28.7 | 29.4 | 42.6 | 42.4 | 33.9 | 44.5 | 1.9 | 0.6 | 15.6 | 6545.1 | 1434.6 | 1101.1 | 5.9 | 5.9 | 10 | 9.9 | 22.2 | 22 | 23 | 24 | 15 | 380
315 | 1 | 0 | 28.8 | 28.7 | 28.8 | 28.7 | 28.7 | 28.8 | 28.7 | 28.8 | 27.5 | 29.4 | 29.5 | 44.4 | 44.5 | 42.7 | 42.5 | 23.2 | 6553.5 | 34 | 33.9 | 33.3 | 42.3 | 42.5 | 28.7 | 28.7 | 28.7 | 28.7 | 29.4 | 42.6 | 42.4 | 33.9 | 44.5 | 1.9 | 0.6 | 15.6 | 6545.1 | 1434.6 | 1101.1 | 5.9 | 5.9 | 10 | 9.9 | 22.2 | 22 | 23 | 24 | 20 | 380
375 | 1 | 0 | 28.9 | 28.9 | 29 | 28.9 | 28.9 | 29 | 28.9 | 29 | 27.8 | 29.6 | 29.7 | 49.3 | 49.6 | 47.2 | 46.9 | 22.3 | 0 | 35.5 | 35.5 | 34.9 | 46.1 | 46.4 | 28.9 | 28.9 | 28.9 | 28.9 | 29.7 | 47.1 | 46.3 | 35.5 | 49.4 | 2.4 | 0.6 | 19.9 | 6542.9 | 1621.5 | 1254.9 | 6.6 | 6.6 | 10 | 9.9 | 22.4 | 22 | 23 | 24 | 20 | 430
375 | 1 | 0 | 28.9 | 28.9 | 29 | 28.9 | 28.9 | 29 | 28.9 | 29 | 27.8 | 29.6 | 29.7 | 49.3 | 49.6 | 47.2 | 46.9 | 22.3 | 0 | 35.5 | 35.5 | 34.9 | 46.1 | 46.4 | 28.9 | 28.9 | 28.9 | 28.9 | 29.7 | 47.1 | 46.3 | 35.5 | 49.4 | 2.4 | 0.6 | 19.9 | 6542.9 | 1621.5 | 1254.9 | 6.6 | 6.6 | 10 | 9.9 | 22.4 | 22 | 23 | 25 | 20 | 430
375 | 1 | 0 | 28.9 | 28.9 | 29 | 28.9 | 28.9 | 29 | 28.9 | 29 | 27.8 | 29.6 | 29.7 | 49.3 | 49.6 | 47.2 | 46.9 | 22.3 | 0 | 35.5 | 35.5 | 34.9 | 46.1 | 46.4 | 28.9 | 28.9 | 28.9 | 28.9 | 29.7 | 47.1 | 46.3 | 35.5 | 49.4 | 2.4 | 0.6 | 19.9 | 6542.9 | 1621.5 | 1254.9 | 6.6 | 6.6 | 10 | 9.9 | 22.4 | 22 | 23 | 25 | 25 | 430
435 | 1 | 0 | 29.3 | 29.2 | 29.3 | 29.3 | 29.3 | 29.3 | 29.2 | 29.3 | 28 | 30.3 | 30.4 | 55.2 | 55.4 | 52.5 | 52.4 | 21.4 | 0 | 37.6 | 37.6 | 37 | 50.8 | 51.1 | 29.2 | 29.3 | 29.3 | 29.2 | 30.3 | 52.5 | 50.9 | 37.6 | 55.3 | 2.8 | 0.6 | 24.7 | 6540.2 | 1847.2 | 1431.8 | 7.5 | 7.4 | 10 | 9.9 | 22.4 | 21.9 | 23 | 25 | 25 | 490
435 | 1 | 0 | 29.3 | 29.2 | 29.3 | 29.3 | 29.3 | 29.3 | 29.2 | 29.3 | 28 | 30.3 | 30.4 | 55.2 | 55.4 | 52.5 | 52.4 | 21.4 | 0 | 37.6 | 37.6 | 37 | 50.8 | 51.1 | 29.2 | 29.3 | 29.3 | 29.2 | 30.3 | 52.5 | 50.9 | 37.6 | 55.3 | 2.8 | 0.6 | 24.7 | 6540.2 | 1847.2 | 1431.8 | 7.5 | 7.4 | 10 | 9.9 | 22.4 | 21.9 | 23 | 27 | 25 | 490
435 | 1 | 0 | 29.3 | 29.2 | 29.3 | 29.3 | 29.3 | 29.3 | 29.2 | 29.3 | 28 | 30.3 | 30.4 | 55.2 | 55.4 | 52.5 | 52.4 | 21.4 | 0 | 37.6 | 37.6 | 37 | 50.8 | 51.1 | 29.2 | 29.3 | 29.3 | 29.2 | 30.3 | 52.5 | 50.9 | 37.6 | 55.3 | 2.8 | 0.6 | 24.7 | 6540.2 | 1847.2 | 1431.8 | 7.5 | 7.4 | 10 | 9.9 | 22.4 | 21.9 | 23 | 27 | 30 | 490
495 | 1 | 0 | 29.7 | 29.7 | 29.8 | 29.7 | 29.7 | 29.8 | 29.7 | 29.7 | 28.3 | 30.9 | 30.9 | 61.3 | 61.6 | 58.3 | 58.3 | 20.2 | 0 | 40 | 39.9 | 39.3 | 55.8 | 56.1 | 29.7 | 29.7 | 29.7 | 29.7 | 30.9 | 58.3 | 56 | 39.9 | 61.4 | 3.1 | 0.6 | 29.9 | 6537.6 | 2025.4 | 1608.6 | 8.2 | 8.2 | 10 | 9.9 | 22.4 | 22 | 23 | 27 | 30 | 515
495 | 1 | 0 | 29.7 | 29.7 | 29.8 | 29.7 | 29.7 | 29.8 | 29.7 | 29.7 | 28.3 | 30.9 | 30.9 | 61.3 | 61.6 | 58.3 | 58.3 | 20.2 | 0 | 40 | 39.9 | 39.3 | 55.8 | 56.1 | 29.7 | 29.7 | 29.7 | 29.7 | 30.9 | 58.3 | 56 | 39.9 | 61.4 | 3.1 | 0.6 | 29.9 | 6537.6 | 2025.4 | 1608.6 | 8.2 | 8.2 | 10 | 9.9 | 22.4 | 22 | 23 | 27 | 30 | 515
495 | 1 | 0 | 29.7 | 29.7 | 29.8 | 29.7 | 29.7 | 29.8 | 29.7 | 29.7 | 28.3 | 30.9 | 30.9 | 61.3 | 61.6 | 58.3 | 58.3 | 20.2 | 0 | 40 | 39.9 | 39.3 | 55.8 | 56.1 | 29.7 | 29.7 | 29.7 | 29.7 | 30.9 | 58.3 | 56 | 39.9 | 61.4 | 3.1 | 0.6 | 29.9 | 6537.6 | 2025.4 | 1608.6 | 8.2 | 8.2 | 10 | 9.9 | 22.4 | 22 | 23 | 27 | 5 | 515
525 | 1 | 0 | 29.8 | 29.8 | 29.9 | 29.8 | 29.8 | 29.9 | 29.8 | 29.8 | 28.5 | 29.7 | 29.8 | 43.2 | 43.2 | 41.5 | 41.4 | 24.2 | 0 | 33.8 | 33.7 | 33.1 | 41.3 | 41.6 | 29.8 | 29.8 | 29.8 | 29.8 | 29.7 | 41.4 | 41.4 | 33.7 | 43.2 | 1.8 | 0.7 | 14.2 | 6545.9 | 1348.4 | 1045.1 | 5.6 | 5.6 | 10 | 9.9 | 22.5 | 22 | 23 | 27 | 5 | 160
525 | 1 | 0 | 29.8 | 29.8 | 29.9 | 29.8 | 29.8 | 29.9 | 29.8 | 29.8 | 28.5 | 29.7 | 29.8 | 43.2 | 43.2 | 41.5 | 41.4 | 24.2 | 0 | 33.8 | 33.7 | 33.1 | 41.3 | 41.6 | 29.8 | 29.8 | 29.8 | 29.8 | 29.7 | 41.4 | 41.4 | 33.7 | 43.2 | 1.8 | 0.7 | 14.2 | 6545.9 | 1348.4 | 1045.1 | 5.6 | 5.6 | 10 | 9.9 | 22.5 | 22 | 23 | 27 | 5 | 160
525 | 1 | 0 | 29.8 | 29.8 | 29.9 | 29.8 | 29.8 | 29.9 | 29.8 | 29.8 | 28.5 | 29.7 | 29.7 | 43.1 | 43.2 | 41.5 | 41.4 | 24.1 | 6553.5 | 33.7 | 33.7 | 33.1 | 41.3 | 41.6 | 29.8 | 29.8 | 29.8 | 29.8 | 29.7 | 41.5 | 41.5 | 33.7 | 43.1 | 1.7 | 0.6 | 14.3 | 6545.9 | 1348.4 | 1042.2 | 5.6 | 5.6 | 10 | 9.9 | 22.5 | 22 | 23 | 27 | 5 | 160

## Decision
Time | Status (0-off 1-on) | Group (0-standalone 1-Group lead 2-Group follow) | TT01 | TT02 | TT31 | TT41 | TT61 | TT62 | TT51 | TT52 | TT45 | PT01 | PT02 | PT31 | PT41 | PT32 | PT42 | PT21 | PT11 | PT51 | PT52 | PT53 | PT61 | PT62 | TT01/TT02 | TT31/TT41 | TT61/TT62 | TT51/TT52 | PT01/PT02 | PT32/PT42 | PT61/PT62 | PT51/PT52 | Pump 31 Filter DP | Pump 41 Filter DP | Primary Filter 53 DP | Secondary DP (Supply - Return) | Primary DP (Supply - Return) | FT01 | FT61 | P31 Speed % | P41 Speed % | FCV61 Actual Flow% | FCV61 Actual Open% | Air Humidity | Air Temperature | Program version | Secondary Temperature Setpoint | Secondary DP Setpoint | Secondary Flow Setpoint
sec | [] | [] | C | C | C | C | PSI | PSI | PSI | PSI | PSI | PSI | PSI | PSI | C | C | PSI | PSI | PSI | PSI | PSI | g/min | % | % | % | % | % | % | % | C | [] | C | PSI | g/min | PSI | PSI | PSI | FT | FT | % | % | % | % | % | C | [] | C | PSI | g/m
15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1
15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0
15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
75 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
75 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
75 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
135 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
135 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
135 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
195 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
195 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
195 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
255 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
255 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
255 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
315 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
315 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
315 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
375 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
375 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
375 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
435 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
435 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
435 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
495 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
495 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
495 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
525 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
525 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1
525 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1

## mean-3Sigma
Time | Status (0-off 1-on) | Group (0-standalone 1-Group lead 2-Group follow) | TT01 | TT02 | TT31 | TT41 | TT61 | TT62 | TT51 | TT52 | TT45 | PT01 | PT02 | PT31 | PT41 | PT32 | PT42 | PT21 | PT11 | PT51 | PT52 | PT53 | PT61 | PT62 | TT01/TT02 | TT31/TT41 | TT61/TT62 | TT51/TT52 | PT01/PT02 | PT32/PT42 | PT61/PT62 | PT51/PT52 | Pump 31 Filter DP | Pump 41 Filter DP | Primary Filter 53 DP | Secondary DP (Supply - Return) | Primary DP (Supply - Return) | FT01 | FT61 | P31 Speed % | P41 Speed % | FCV61 Actual Flow% | FCV61 Actual Open% | Air Humidity | Air Temperature | Program version | Secondary Temperature Setpoint | Secondary DP Setpoint | Secondary Flow Setpoint
15 | 1 | 0 | 17.1267 | 17.0931 | 17.1551 | 17.1239 | 17.1364 | 17.0924 | 17.1696 | 17.1506 | 16.9465 | 20.1586 | 20.0995 | 31.4863 | 31.772 | 29.643 | 29.8391 | 13.5251 | -6972.306 | 30.4246 | 30.5992 | 28.93 | -2008.0698 | 21.5235 | 17.0908 | 17.1259 | 17.0779 | 17.1603 | 20.1318 | 29.7691 | 21.5175 | 30.4821 | 31.6417 | 0.4 | 1.2044 | -2033.4862 | -2038.3009 | 790.1486 | -451.4037 | 3.7159 | 3.7308 | 5.1838 | -2826.0998 | -7.125 | -2024.4018 | 15 | 15.0441 | 5 | -23.5245
75 | 1 | 0 | 17.3559 | 17.3279 | 17.4128 | 17.3816 | 17.3698 | 17.3385 | 17.3886 | 17.4158 | 17.0603 | 20.7401 | 20.6863 | 31.8369 | 32.2941 | 29.9145 | 30.0787 | 15.1593 | -6927.625 | 30.7398 | 30.8983 | 29.2252 | -2008.6445 | 21.6531 | 17.3429 | 17.376 | 17.3466 | 17.3843 | 20.7092 | 30.0549 | 21.6587 | 30.8525 | 32.083 | 0.4 | 1.0895 | 10.4267 | 7.914 | 1040.5353 | -498.8171 | 5.1298 | 5.1298 | 5.1868 | -2826.0332 | -7.2841 | -2024.3814 | 15 | 21 | 5 | 160
75 | 1 | 0 | 17.3559 | 17.3279 | 17.4128 | 17.3864 | 17.3732 | 17.3441 | 17.3886 | 17.4158 | 17.0603 | 20.752 | 20.6952 | 31.8359 | 32.2956 | 29.9131 | 30.0737 | 15.155 | -6927.6284 | 30.7411 | 30.8977 | 29.2251 | -2008.6429 | 21.6608 | 17.3429 | 17.376 | 17.3514 | 17.3843 | 20.7203 | 30.0531 | 21.6642 | 30.8504 | 32.0851 | 0.4 | 1.0895 | 10.4267 | 7.9133 | 1040.5188 | -498.8343 | 5.1298 | 5.1298 | 5.1868 | -2826.035 | -7.2841 | -2024.383 | 15 | 21 | 5 | 160
75 | 1 | 0 | 17.3559 | 17.3279 | 17.4128 | 17.3864 | 17.3732 | 17.3507 | 17.3939 | 17.4158 | 17.0603 | 20.7423 | 20.6909 | 31.8404 | 32.303 | 29.9227 | 30.0798 | 15.1646 | -6927.6317 | 30.7521 | 30.9103 | 29.2203 | -2008.6413 | 21.6608 | 17.3429 | 17.376 | 17.3514 | 17.3895 | 20.7205 | 30.0656 | 21.6693 | 30.8538 | 32.0954 | 0.4 | 1.0895 | 10.4414 | 7.9147 | 1040.7482 | -499.0096 | 5.1298 | 5.1298 | 5.1868 | -2826.035 | -7.2841 | -2024.383 | 15 | 21 | 10 | 160
135 | 1 | 0 | 17.5949 | 17.5773 | 17.6357 | 17.6304 | 17.6304 | 17.5786 | 17.6539 | 17.6523 | 17.1921 | 20.721 | 20.6957 | 32.2666 | 32.6008 | 30.2571 | 30.4319 | 15.0716 | -7009.1256 | 31.0241 | 31.1986 | 29.496 | -2008.6033 | 21.7078 | 17.5859 | 17.6192 | 17.5987 | 17.6445 | 20.6977 | 30.4045 | 21.692 | 31.1249 | 32.4961 | 0.5 | 1.0855 | 10.9573 | 8.324 | 1031.2666 | -499.7698 | 4.785 | 4.785 | 5.1875 | -2826.0332 | -7.2532 | -2024.3127 | 15 | 21 | 10 | 320
135 | 1 | 0 | 17.599 | 17.5773 | 17.6357 | 17.6304 | 17.6348 | 17.5786 | 17.6539 | 17.6564 | 17.1921 | 20.721 | 20.7006 | 32.2958 | 32.6279 | 30.2755 | 30.4479 | 15.0736 | -7009.1256 | 31.0374 | 31.2258 | 29.5218 | -2008.6018 | 21.6987 | 17.5899 | 17.6155 | 17.5987 | 17.6445 | 20.7022 | 30.4196 | 21.694 | 31.1579 | 32.4936 | 0.5 | 1.0904 | 10.9538 | 8.3246 | 1031.139 | -499.6425 | 4.785 | 4.785 | 5.1875 | -2826.0332 | -7.244 | -2024.3127 | 15 | 22 | 10 | 320
135 | 1 | 0 | 17.599 | 17.5773 | 17.6357 | 17.6267 | 17.6348 | 17.5786 | 17.6539 | 17.6584 | 17.1921 | 20.7267 | 20.7025 | 32.3045 | 32.6405 | 30.2793 | 30.4292 | 15.0687 | -7009.1256 | 31.0398 | 31.2338 | 29.5214 | -2008.6018 | 21.6973 | 17.5916 | 17.6137 | 17.5987 | 17.6445 | 20.7093 | 30.4173 | 21.6862 | 31.1594 | 32.5122 | 0.5 | 1.0904 | 10.9565 | 8.3302 | 1031.0758 | -499.7565 | 4.785 | 4.785 | 5.1875 | -2826.0332 | -7.242 | -2024.3127 | 15 | 22 | 19.9408 | 320
195 | 1 | 0 | 18.0709 | 18.0546 | 18.15 | 18.0971 | 18.0917 | 18.0572 | 18.1214 | 18.1629 | 17.437 | 22.0367 | 22.0113 | 42.6858 | 43.3811 | 40.2086 | 40.255 | 12.9613 | -6927.6284 | 39.9148 | 39.9562 | 37.5198 | -2005.0706 | 23.9249 | 18.0495 | 18.1052 | 18.06 | 18.1282 | 22.0368 | 40.2875 | 23.9583 | 39.9264 | 43.0721 | 0.6 | 1.9872 | 18.9917 | 14.5483 | 1425.313 | 3.9804 | 6.7525 | 6.645 | 5.1875 | -2826.0315 | -6.9259 | -2024.3174 | 15 | 22 | 25 | 480
195 | 1 | 0 | 18.0736 | 18.0582 | 18.1525 | 18.0997 | 18.0926 | 18.0572 | 18.1256 | 18.1654 | 17.437 | 22.055 | 22.0156 | 42.6933 | 43.386 | 40.2222 | 40.2668 | 12.985 | -6972.3165 | 39.9273 | 39.968 | 37.5297 | -2005.0657 | 23.938 | 18.0506 | 18.1052 | 18.06 | 18.1295 | 22.0604 | 40.2987 | 23.9696 | 39.9297 | 43.0676 | 0.6 | 1.9872 | 18.9917 | 14.5498 | 1425.9931 | 4.0782 | 6.7525 | 6.645 | 5.1875 | -2826.0315 | -6.9259 | -2024.3174 | 15 | 22.6627 | 25 | 480
195 | 1 | 0 | 18.0736 | 18.0582 | 18.1525 | 18.0997 | 18.0926 | 18.0572 | 18.124 | 18.1634 | 17.437 | 22.0591 | 22.0109 | 42.7003 | 43.3839 | 40.2284 | 40.2701 | 12.9858 | -6972.3199 | 39.9329 | 39.9738 | 37.5339 | -2005.0657 | 23.9381 | 18.0506 | 18.0992 | 18.06 | 18.1295 | 22.0606 | 40.3047 | 23.9733 | 39.9351 | 43.0691 | 0.6 | 1.989 | 18.9947 | 14.5482 | 1426.1055 | 4.1092 | 6.7525 | 6.645 | 5.1875 | -2826.0315 | -6.9216 | -2024.3174 | 15 | 23 | 28.2604 | 480
255 | 1 | 0 | 18.8743 | 18.8522 | 18.9411 | 18.9143 | 18.8937 | 18.849 | 18.9246 | 18.9541 | 17.8622 | 23.1483 | 23.0504 | 47.9708 | 48.898 | 45.0479 | 45.0588 | 11.7297 | -6972.3186 | 44.4065 | 44.395 | 41.64 | -2002.2238 | 25.415 | 18.8469 | 18.9168 | 18.8534 | 18.9177 | 23.0826 | 45.1054 | 25.4592 | 44.3971 | 48.46 | 0.4 | 2.3787 | 22.6842 | 17.581 | 1664.5299 | 262.9544 | 7.7096 | 7.6279 | 5.1875 | -2826.0332 | -6.7959 | -2024.2826 | 15 | 23 | 33 | 560
255 | 1 | 0 | 18.8757 | 18.8522 | 18.943 | 18.9143 | 18.8952 | 18.8545 | 18.9246 | 18.9596 | 17.8663 | 23.1416 | 23.0554 | 47.9536 | 48.89 | 45.0327 | 45.0438 | 11.7541 | -6972.3186 | 44.3979 | 44.3886 | 41.6305 | -2002.2286 | 25.4047 | 18.8514 | 18.9168 | 18.8586 | 18.9225 | 23.0803 | 45.0903 | 25.4429 | 44.3921 | 48.4509 | 0.4 | 2.385 | 22.6796 | 17.582 | 1664.5327 | 262.7512 | 7.7096 | 7.6279 | 5.1875 | -2826.0332 | -6.7959 | -2024.2826 | 15 | 23 | 33 | 560
255 | 1 | 0 | 18.8793 | 18.8522 | 18.943 | 18.9161 | 18.8952 | 18.8545 | 18.9255 | 18.9596 | 17.8663 | 23.1181 | 23.0371 | 47.9779 | 48.8997 | 45.0403 | 45.0416 | 11.7247 | -6972.3186 | 44.391 | 44.386 | 41.6293 | -2002.2191 | 25.393 | 18.8532 | 18.9128 | 18.8609 | 18.9217 | 23.0504 | 45.0866 | 25.428 | 44.3845 | 48.553 | 2.3 | 2.3846 | 22.6896 | 17.5821 | 1664.7381 | 262.8179 | 7.7096 | 7.6279 | 5.1875 | -2826.0332 | -6.8137 | -2024.2826 | 15 | 23 | 15 | 560
315 | 1 | 0 | 19.3363 | 19.3092 | 19.3918 | 19.3558 | 19.3579 | 19.3086 | 19.3721 | 19.3963 | 18.3551 | 21.0363 | 21.0476 | 35.5189 | 36.1188 | 33.6161 | 33.6986 | 14.6122 | -6927.6202 | 33.8438 | 33.9997 | 32.0411 | -2007.4534 | 22.2831 | 19.311 | 19.3623 | 19.3131 | 19.3539 | 21.0654 | 33.7147 | 22.3032 | 33.9321 | 35.8397 | 0.3 | 1.3796 | 14.3125 | 10.6041 | 1179.7469 | -323.237 | 5.1077 | 4.9845 | 5.1868 | -2826.0332 | -6.9084 | -2024.3891 | 15 | 23 | 15 | 380
315 | 1 | 0 | 19.3385 | 19.3131 | 19.3918 | 19.3559 | 19.3579 | 19.311 | 19.3712 | 19.3963 | 18.3551 | 21.0486 | 21.0503 | 35.5179 | 36.1066 | 33.6105 | 33.6939 | 14.6046 | -6927.6202 | 33.8436 | 33.9862 | 32.0286 | -2007.4565 | 22.3072 | 19.315 | 19.3623 | 19.3155 | 19.3539 | 21.0682 | 33.7146 | 22.3183 | 33.9382 | 35.8377 | 0.3 | 1.3776 | 14.3096 | 10.5845 | 1179.805 | -323.6208 | 5.1077 | 4.9845 | 5.1868 | -2826.0315 | -6.9084 | -2024.3891 | 15 | 23.6627 | 15 | 380
315 | 1 | 0 | 19.3385 | 19.3095 | 19.3918 | 19.3559 | 19.3542 | 19.311 | 19.3712 | 19.3963 | 18.3551 | 21.0447 | 21.0467 | 35.5194 | 36.1063 | 33.6105 | 33.6966 | 14.6046 | -6927.6202 | 33.8436 | 33.9862 | 32.0253 | -2007.4565 | 22.3072 | 19.315 | 19.3623 | 19.3155 | 19.3539 | 21.0644 | 33.7169 | 22.3163 | 33.9355 | 35.8377 | 0.3 | 1.3779 | 14.3087 | 10.5792 | 1179.2442 | -323.7708 | 5.1072 | 4.984 | 5.1868 | -2826.0315 | -6.8961 | -2024.3891 | 15 | 24 | 18.3136 | 380
375 | 1 | 0 | 19.7092 | 19.6879 | 19.7704 | 19.7306 | 19.7339 | 19.704 | 19.7489 | 19.7523 | 18.6996 | 21.6396 | 21.6259 | 39.157 | 39.8967 | 36.9855 | 36.9774 | 13.9812 | -7009.1518 | 36.9172 | 37.0082 | 34.8168 | -2006.2587 | 23.1364 | 19.6952 | 19.7389 | 19.7115 | 19.7575 | 21.6428 | 37.0391 | 23.1521 | 36.9735 | 39.5547 | 0.1 | 1.6346 | 16.5051 | 12.5487 | 1286.2365 | -174.9847 | 5.9261 | 5.8137 | 5.1875 | -2826.0315 | -6.885 | -2024.3986 | 15 | 24 | 20 | 430
375 | 1 | 0 | 19.7092 | 19.6879 | 19.7704 | 19.7306 | 19.7334 | 19.704 | 19.7489 | 19.7518 | 18.7054 | 21.6509 | 21.6385 | 39.1581 | 39.9057 | 36.9884 | 36.976 | 13.9876 | -7038.4262 | 36.9124 | 37.0079 | 34.8299 | -2006.2572 | 23.1369 | 19.6952 | 19.7389 | 19.7115 | 19.7575 | 21.6528 | 37.054 | 23.1552 | 36.9756 | 39.5676 | 0.1 | 1.6294 | 16.5076 | 12.5503 | 1286.1303 | -174.9086 | 5.9261 | 5.8137 | 5.1875 | -2826.0315 | -6.884 | -2024.3986 | 15 | 24.6627 | 20 | 430
375 | 1 | 0 | 19.7092 | 19.6894 | 19.7704 | 19.7306 | 19.7334 | 19.7022 | 19.7489 | 19.7518 | 18.7054 | 21.6483 | 21.6424 | 39.1709 | 39.9267 | 36.9986 | 36.9873 | 13.9947 | -7060.4053 | 36.9249 | 37.0214 | 34.8405 | -2006.2572 | 23.1468 | 19.6967 | 19.7389 | 19.7115 | 19.7592 | 21.6603 | 37.0593 | 23.1596 | 36.9896 | 39.5721 | 0.1 | 1.6322 | 16.5082 | 12.5547 | 1286.1839 | -174.6564 | 5.9261 | 5.8137 | 5.1875 | -2826.0315 | -6.884 | -2024.3986 | 15 | 24.6627 | 22.5941 | 430
435 | 1 | 0 | 20.2346 | 20.2151 | 20.2979 | 20.2605 | 20.2633 | 20.2131 | 20.301 | 20.2965 | 19.1265 | 22.3476 | 22.2897 | 42.964 | 43.8181 | 40.5318 | 40.509 | 13.1593 | -6927.6136 | 40.2312 | 40.2403 | 37.8441 | -2004.5502 | 24.1788 | 20.2094 | 20.2721 | 20.231 | 20.2677 | 22.317 | 40.5748 | 24.2358 | 40.2501 | 43.4112 | 0.3 | 1.9814 | 19.0813 | 14.6354 | 1431.1425 | 20.9373 | 6.8172 | 6.7063 | 5.1875 | -2826.0315 | -6.8351 | -2024.4847 | 15 | 25 | 25 | 490
435 | 1 | 0 | 20.2346 | 20.2151 | 20.2979 | 20.2605 | 20.2633 | 20.2131 | 20.3009 | 20.2965 | 19.1233 | 22.3313 | 22.2791 | 42.9614 | 43.8075 | 40.5224 | 40.5042 | 13.1565 | -6927.6136 | 40.228 | 40.2365 | 37.8396 | -2004.5454 | 24.1775 | 20.2142 | 20.2721 | 20.231 | 20.2677 | 22.3048 | 40.5712 | 24.2366 | 40.2521 | 43.4094 | 0.3 | 1.9836 | 19.0797 | 14.6362 | 1431.5275 | 20.9752 | 6.8172 | 6.7063 | 5.1875 | -2826.0315 | -6.8351 | -2024.4847 | 15 | 27 | 25 | 490
435 | 1 | 0 | 20.2346 | 20.221 | 20.2979 | 20.2605 | 20.263 | 20.2104 | 20.3009 | 20.2965 | 19.1233 | 22.3298 | 22.2744 | 42.9633 | 43.8123 | 40.5381 | 40.5156 | 13.1392 | -6927.6169 | 40.2304 | 40.2351 | 37.8429 | -2004.5391 | 24.168 | 20.2123 | 20.2721 | 20.2279 | 20.2677 | 22.2982 | 40.5813 | 24.22 | 40.2497 | 43.4162 | 0.3 | 1.9813 | 19.0837 | 14.6348 | 1431.7335 | 21.0883 | 6.8172 | 6.7063 | 5.1875 | -2826.0315 | -6.8423 | -2024.4831 | 15 | 27 | 28.3136 | 490
495 | 1 | 0 | 20.9481 | 20.9166 | 21.0207 | 20.9676 | 20.9627 | 20.9217 | 21.0108 | 21.0084 | 19.6268 | 22.9822 | 22.9162 | 46.7678 | 47.4094 | 43.9786 | 43.8787 | 12.3397 | -6927.6302 | 43.3202 | 43.327 | 40.6761 | -2002.6762 | 25.1206 | 20.9462 | 20.9712 | 20.9129 | 20.9908 | 22.947 | 43.9681 | 25.1272 | 43.3428 | 47.1162 | 0.2 | 2.2611 | 21.7218 | 16.7399 | 1584.8736 | 190.3966 | 7.4531 | 7.3981 | 5.1875 | -2826.0315 | -6.6793 | -2024.4598 | 15 | 27 | 30 | 515
495 | 1 | 0 | 20.9474 | 20.9182 | 21.0207 | 20.9676 | 20.9627 | 20.9217 | 21.0108 | 21.0084 | 19.6268 | 22.9811 | 22.9059 | 46.7256 | 47.3941 | 43.9652 | 43.8644 | 12.3416 | -6972.3186 | 43.3097 | 43.3163 | 40.6607 | -2002.6778 | 25.123 | 20.947 | 20.973 | 20.9129 | 20.995 | 22.9631 | 43.9557 | 25.1417 | 43.3332 | 47.1056 | 0.2 | 2.2611 | 21.719 | 16.734 | 1585.0383 | 190.5829 | 7.4531 | 7.3981 | 5.1875 | -2826.0315 | -6.6793 | -2024.4598 | 15 | 27 | 30 | 515
495 | 1 | 0 | 20.9474 | 20.9189 | 21.0207 | 20.9676 | 20.96 | 20.9217 | 21.015 | 21.0084 | 19.6273 | 22.9809 | 22.9018 | 46.6008 | 47.3881 | 43.9459 | 43.8917 | 12.3547 | -6972.3288 | 43.3112 | 43.3183 | 40.6613 | -2002.6746 | 25.1441 | 20.947 | 20.973 | 20.9129 | 20.995 | 22.9559 | 43.9611 | 25.1508 | 43.3357 | 47.041 | 0.2 | 2.259 | 21.7187 | 16.7088 | 1585.0903 | 190.5649 | 7.4531 | 7.3981 | 5.1875 | -2826.0315 | -6.6793 | -2024.4614 | 15 | 27 | -2.8367 | 515
525 | 1 | 0 | 21.1404 | 21.106 | 21.1918 | 21.1392 | 21.1337 | 21.0868 | 21.1707 | 21.1789 | 19.8876 | 20.922 | 20.8884 | 32.4379 | 32.8164 | 30.5147 | 30.6236 | 15.3086 | -6813.2593 | 31.2334 | 31.4161 | 29.7151 | -2007.8651 | 21.864 | 21.1155 | 21.1496 | 21.1191 | 21.1661 | 20.9214 | 30.6236 | 21.8656 | 31.346 | 32.6664 | 0.1 | 1.1139 | 10.9013 | 8.2558 | 1047.8861 | -479.4413 | 4.785 | 4.7536 | 5.1875 | -2826.0315 | -7.0754 | -2024.4237 | 15 | 27 | 5 | 160
525 | 1 | 0 | 21.1404 | 21.106 | 21.1918 | 21.1392 | 21.1337 | 21.0868 | 21.1773 | 21.1789 | 19.8876 | 20.9268 | 20.899 | 32.437 | 32.8141 | 30.5169 | 30.6322 | 15.3159 | -6813.2593 | 31.2258 | 31.4191 | 29.7076 | -2007.8651 | 21.8704 | 21.1155 | 21.1496 | 21.1191 | 21.1661 | 20.9278 | 30.6296 | 21.8685 | 31.346 | 32.6705 | 0.1 | 1.1149 | 10.9072 | 8.2558 | 1047.3331 | -479.6929 | 4.785 | 4.7536 | 5.1875 | -2826.0315 | -7.0754 | -2024.4237 | 15 | 27 | 5 | 160
525 | 1 | 0 | 21.1404 | 21.106 | 21.1918 | 21.1429 | 21.1337 | 21.0868 | 21.1773 | 21.1789 | 19.8876 | 20.9296 | 20.9058 | 32.435 | 32.8283 | 30.5297 | 30.6394 | 15.3184 | -6813.2625 | 31.245 | 31.4281 | 29.7098 | -2007.8635 | 21.867 | 21.1155 | 21.1554 | 21.1191 | 21.1661 | 20.9365 | 30.6375 | 21.8685 | 31.3504 | 32.6672 | 0.1 | 1.1103 | 10.9021 | 8.2516 | 1047.3717 | -480.1321 | 4.785 | 4.7536 | 5.1875 | -2826.0315 | -7.0739 | -2024.4237 | 15 | 27 | -4.2901 | 160

## mean+3Sigma
Time | Status (0-off 1-on) | Group (0-standalone 1-Group lead 2-Group follow) | TT01 | TT02 | TT31 | TT41 | TT61 | TT62 | TT51 | TT52 | TT45 | PT01 | PT02 | PT31 | PT41 | PT32 | PT42 | PT21 | PT11 | PT51 | PT52 | PT53 | PT61 | PT62 | TT01/TT02 | TT31/TT41 | TT61/TT62 | TT51/TT52 | PT01/PT02 | PT32/PT42 | PT61/PT62 | PT51/PT52 | Pump 31 Filter DP | Pump 41 Filter DP | Primary Filter 53 DP | Secondary DP (Supply - Return) | Primary DP (Supply - Return) | FT01 | FT61 | P31 Speed % | P41 Speed % | FCV61 Actual Flow% | FCV61 Actual Open% | Air Humidity | Air Temperature | Program version | Secondary Temperature Setpoint | Secondary DP Setpoint | Secondary Flow Setpoint
15 | 1 | 0 | 37.3923 | 37.4379 | 37.3925 | 37.3785 | 37.3565 | 37.4148 | 37.3423 | 37.3827 | 35.8035 | 30.3034 | 30.2314 | 50.2851 | 50.4566 | 47.0141 | 46.9347 | 23.7963 | 10561.1893 | 46.9873 | 46.815 | 44.4962 | 2215.8032 | 31.917 | 37.4116 | 37.3693 | 37.3911 | 37.3254 | 30.2611 | 46.9309 | 31.8111 | 46.9179 | 50.3417 | 4.0285 | 2.7695 | 2220.86 | 2218.4294 | 2357.7133 | 3176.6347 | 8.6103 | 8.5978 | 14.3281 | 3157.3903 | 42.6369 | 2225.2399 | 15 | 27.4083 | 5 | 243.7626
75 | 1 | 0 | 37.5703 | 37.6126 | 37.5634 | 37.5732 | 37.5183 | 37.5711 | 37.5685 | 37.558 | 36.1349 | 29.4384 | 29.3685 | 43.4179 | 43.3393 | 40.7831 | 40.7498 | 23.7312 | 10360.4846 | 41.434 | 41.2945 | 39.4748 | 2215.5111 | 30.9231 | 37.5666 | 37.5597 | 37.5273 | 37.5515 | 29.4003 | 40.688 | 30.7984 | 41.3165 | 43.3598 | 3.4627 | 2.389 | 15.2376 | 11.8121 | 1885.5766 | 3006.6504 | 6.1059 | 6.1059 | 14.3323 | 3157.4142 | 42.6294 | 2225.2504 | 15 | 21 | 5 | 160
75 | 1 | 0 | 37.5703 | 37.6126 | 37.5634 | 37.5708 | 37.5173 | 37.5701 | 37.5685 | 37.558 | 36.1349 | 29.4266 | 29.3596 | 43.4188 | 43.3377 | 40.7892 | 40.762 | 23.7354 | 10360.4855 | 41.4446 | 41.3047 | 39.4773 | 2215.5119 | 30.9154 | 37.5666 | 37.5597 | 37.5247 | 37.5515 | 29.3916 | 40.7041 | 30.7858 | 41.3258 | 43.3601 | 3.4637 | 2.389 | 15.2423 | 11.8105 | 1885.486 | 3006.601 | 6.1059 | 6.1059 | 14.3323 | 3157.4136 | 42.6294 | 2225.2497 | 15 | 21 | 5 | 160
75 | 1 | 0 | 37.5703 | 37.6126 | 37.5634 | 37.5708 | 37.5173 | 37.5659 | 37.5657 | 37.558 | 36.1349 | 29.4316 | 29.3591 | 43.4262 | 43.3422 | 40.7963 | 40.7654 | 23.7235 | 10360.4864 | 41.4384 | 41.2992 | 39.4821 | 2215.5127 | 30.9154 | 37.5666 | 37.5597 | 37.5247 | 37.5486 | 29.3914 | 40.7106 | 30.7854 | 41.3296 | 43.3617 | 3.4653 | 2.389 | 15.2443 | 11.8044 | 1885.4899 | 3006.5357 | 6.1059 | 6.1059 | 14.3323 | 3157.4136 | 42.6294 | 2225.2497 | 15 | 21 | 10 | 160
135 | 1 | 0 | 37.7456 | 37.7775 | 37.7453 | 37.7387 | 37.6815 | 37.7571 | 37.7175 | 37.7381 | 36.3627 | 29.4933 | 29.4114 | 43.1024 | 43.1611 | 40.5619 | 40.5347 | 23.8451 | 10754.0566 | 41.264 | 41.1038 | 39.3159 | 2215.5319 | 30.9255 | 37.7403 | 37.7285 | 37.7036 | 37.6984 | 29.457 | 40.4812 | 30.8175 | 41.168 | 43.0706 | 3.4129 | 2.3788 | 14.8022 | 11.4474 | 1888.9596 | 3005.2484 | 6.4769 | 6.4769 | 14.3339 | 3157.4142 | 42.4627 | 2225.1865 | 15 | 21 | 10 | 320
135 | 1 | 0 | 37.7439 | 37.7775 | 37.7453 | 37.7387 | 37.6795 | 37.7571 | 37.7175 | 37.7365 | 36.3627 | 29.4933 | 29.4065 | 43.0875 | 43.1483 | 40.553 | 40.514 | 23.8479 | 10754.0566 | 41.2531 | 41.0837 | 39.2949 | 2215.5327 | 30.9346 | 37.7387 | 37.7345 | 37.7036 | 37.6984 | 29.455 | 40.4613 | 30.8227 | 41.1398 | 43.073 | 3.4184 | 2.3738 | 14.7986 | 11.4397 | 1889.1205 | 3005.2902 | 6.4769 | 6.4769 | 14.3339 | 3157.4142 | 42.4488 | 2225.1865 | 15 | 22 | 10 | 320
135 | 1 | 0 | 37.7439 | 37.7775 | 37.7453 | 37.7447 | 37.6795 | 37.7571 | 37.7175 | 37.7368 | 36.3627 | 29.4899 | 29.4094 | 43.0788 | 43.1428 | 40.5493 | 40.5351 | 23.8599 | 10754.0566 | 41.2483 | 41.0781 | 39.2977 | 2215.5327 | 30.936 | 37.7393 | 37.7339 | 37.7036 | 37.6984 | 29.4502 | 40.4732 | 30.8304 | 41.1383 | 43.0688 | 3.4166 | 2.3738 | 14.8007 | 11.4389 | 1889.1813 | 3005.2303 | 6.4769 | 6.4769 | 14.3339 | 3157.4142 | 42.4492 | 2225.1865 | 15 | 22 | 29.702 | 320
195 | 1 | 0 | 38.1314 | 38.1811 | 38.1572 | 38.1624 | 38.1011 | 38.1499 | 38.1524 | 38.1324 | 36.6368 | 31.3204 | 31.1697 | 60.8857 | 61.0808 | 56.5747 | 56.645 | 21.2125 | 10360.4855 | 55.5376 | 55.5081 | 52.3755 | 2217.3158 | 33.9632 | 38.141 | 38.1591 | 38.1042 | 38.1408 | 31.218 | 56.5554 | 33.8726 | 55.5165 | 60.9588 | 5.1053 | 3.5675 | 29.6202 | 23.0827 | 2571.5299 | 3330.4554 | 8.6808 | 8.7907 | 14.3339 | 3157.4148 | 42.0164 | 2225.1841 | 15 | 22 | 25 | 480
195 | 1 | 0 | 38.1335 | 38.1799 | 38.157 | 38.1622 | 38.1027 | 38.1499 | 38.1505 | 38.1322 | 36.6368 | 31.3021 | 31.1582 | 60.8901 | 61.0759 | 56.5706 | 56.6356 | 21.1983 | 10561.2093 | 55.5299 | 55.501 | 52.3655 | 2217.3181 | 33.9477 | 38.1423 | 38.1591 | 38.1042 | 38.1419 | 31.1968 | 56.5513 | 33.8637 | 55.5132 | 60.9586 | 5.1023 | 3.5675 | 29.6154 | 23.0812 | 2571.1236 | 3330.4956 | 8.6808 | 8.7907 | 14.3339 | 3157.4148 | 42.0164 | 2225.1841 | 15 | 23.3135 | 25 | 480
195 | 1 | 0 | 38.1335 | 38.1799 | 38.157 | 38.1622 | 38.1027 | 38.1499 | 38.1545 | 38.1366 | 36.6368 | 31.3005 | 31.1677 | 60.883 | 61.0804 | 56.5597 | 56.6394 | 21.1952 | 10561.2103 | 55.529 | 55.5 | 52.359 | 2217.3181 | 33.9452 | 38.1423 | 38.1674 | 38.1042 | 38.1419 | 31.1965 | 56.5524 | 33.8624 | 55.5125 | 60.9642 | 5.0986 | 3.5705 | 29.622 | 23.0875 | 2571.1826 | 3330.5646 | 8.6808 | 8.7907 | 14.3339 | 3157.4148 | 42.0121 | 2225.1841 | 15 | 23 | 37.1681 | 480
255 | 1 | 0 | 38.8305 | 38.8811 | 38.8875 | 38.8762 | 38.8015 | 38.8652 | 38.8849 | 38.8697 | 37.1021 | 33.0874 | 32.9639 | 74.5649 | 75.1496 | 69.5164 | 69.5936 | 20.1512 | 10561.2043 | 66.953 | 66.9574 | 62.7696 | 2218.7548 | 36.6683 | 38.8365 | 38.8642 | 38.8228 | 38.868 | 33.0317 | 69.4993 | 36.648 | 66.9577 | 74.8209 | 6.1908 | 4.5713 | 40.8277 | 31.669 | 2772.6177 | 3528.4956 | 9.9761 | 9.9626 | 14.3339 | 3157.4142 | 41.7435 | 2225.1516 | 15 | 23 | 33 | 560
255 | 1 | 0 | 38.8338 | 38.8811 | 38.888 | 38.8762 | 38.8048 | 38.8621 | 38.8849 | 38.8666 | 37.1004 | 33.0918 | 32.9637 | 74.5583 | 75.1458 | 69.5173 | 69.5777 | 20.1411 | 10561.2043 | 66.9473 | 66.9518 | 62.7624 | 2218.7524 | 36.6715 | 38.8367 | 38.8642 | 38.8224 | 38.8656 | 33.0316 | 69.4906 | 36.6524 | 66.9531 | 74.8158 | 6.1939 | 4.5721 | 40.8109 | 31.6656 | 2772.6483 | 3528.4607 | 9.9761 | 9.9626 | 14.3339 | 3157.4142 | 41.7435 | 2225.1516 | 15 | 23 | 33 | 560
255 | 1 | 0 | 38.835 | 38.8811 | 38.888 | 38.8768 | 38.8048 | 38.8621 | 38.8888 | 38.8666 | 37.1004 | 33.1129 | 32.9844 | 74.5792 | 75.1622 | 69.5359 | 69.5965 | 20.1753 | 10561.2043 | 66.9614 | 66.9616 | 62.7683 | 2218.7572 | 36.7022 | 38.8397 | 38.8705 | 38.8248 | 38.8712 | 33.0686 | 69.5253 | 36.6911 | 66.975 | 74.8137 | 5.7767 | 4.5797 | 40.8223 | 31.6679 | 2772.75 | 3528.3607 | 9.9761 | 9.9626 | 14.3339 | 3157.4142 | 41.7637 | 2225.1516 | 15 | 23 | 15 | 560
315 | 1 | 0 | 39.2494 | 39.3051 | 39.2724 | 39.2632 | 39.204 | 39.27 | 39.2588 | 39.2489 | 37.5521 | 30.3399 | 30.2 | 47.4335 | 47.3859 | 44.2482 | 44.2395 | 23.4163 | 10360.4774 | 44.749 | 44.6169 | 42.5566 | 2216.1129 | 32.0526 | 39.2675 | 39.2568 | 39.2274 | 39.2628 | 30.2489 | 44.1734 | 31.9468 | 44.6584 | 47.3746 | 3.9279 | 2.6251 | 17.2779 | 13.7316 | 2136.2674 | 3119.2537 | 7.4281 | 7.5536 | 14.3323 | 3157.4142 | 41.8631 | 2225.2462 | 15 | 23 | 15 | 380
315 | 1 | 0 | 39.2496 | 39.3036 | 39.2724 | 39.268 | 39.204 | 39.27 | 39.2621 | 39.2489 | 37.5521 | 30.3204 | 30.195 | 47.4273 | 47.3839 | 44.2371 | 44.2275 | 23.4264 | 10360.4774 | 44.7397 | 44.6138 | 42.5595 | 2216.1113 | 32.0356 | 39.2659 | 39.2615 | 39.2274 | 39.2628 | 30.2438 | 44.1616 | 31.9293 | 44.6499 | 47.3623 | 3.9174 | 2.6248 | 17.2785 | 13.7441 | 2135.4521 | 3119.0922 | 7.4281 | 7.5536 | 14.3323 | 3157.4148 | 41.8631 | 2225.2462 | 15 | 24.3135 | 15 | 380
315 | 1 | 0 | 39.2496 | 39.3095 | 39.2724 | 39.268 | 39.21 | 39.27 | 39.2621 | 39.2489 | 37.5521 | 30.3244 | 30.1985 | 47.4235 | 47.3794 | 44.2371 | 44.2225 | 23.4264 | 10360.4774 | 44.7397 | 44.6138 | 42.5628 | 2216.1113 | 32.0356 | 39.2659 | 39.2615 | 39.2274 | 39.2628 | 30.2475 | 44.1569 | 31.9337 | 44.6502 | 47.3623 | 3.92 | 2.6268 | 17.2699 | 13.747 | 2135.6035 | 3118.8661 | 7.4261 | 7.5517 | 14.3323 | 3157.4148 | 41.8485 | 2225.2462 | 15 | 24 | 21.5673 | 380
375 | 1 | 0 | 39.5813 | 39.6264 | 39.5915 | 39.6122 | 39.5304 | 39.5864 | 39.5963 | 39.6 | 37.9147 | 30.8104 | 30.6812 | 53.3596 | 53.3152 | 49.6764 | 49.7679 | 22.4641 | 10754.0756 | 49.5233 | 49.4489 | 46.9023 | 2216.7159 | 32.9994 | 39.5833 | 39.5849 | 39.5409 | 39.5663 | 30.7453 | 49.6443 | 32.8979 | 49.4575 | 53.3048 | 4.503 | 3.0868 | 22.8306 | 17.837 | 2348.4373 | 3212.0537 | 7.9905 | 8.1078 | 14.3339 | 3157.4148 | 41.8207 | 2225.2415 | 15 | 24 | 20 | 430
375 | 1 | 0 | 39.5813 | 39.6264 | 39.5915 | 39.6122 | 39.5333 | 39.5864 | 39.5963 | 39.6054 | 37.9136 | 30.7991 | 30.6734 | 53.3633 | 53.3157 | 49.6807 | 49.7811 | 22.46 | 10939.3881 | 49.5304 | 49.4468 | 46.9034 | 2216.7167 | 33.0036 | 39.5833 | 39.5849 | 39.5409 | 39.5663 | 30.7376 | 49.6508 | 32.9044 | 49.4601 | 53.3014 | 4.4911 | 3.0825 | 22.8424 | 17.8354 | 2348.5768 | 3212.1158 | 7.9905 | 8.1078 | 14.3339 | 3157.4148 | 41.8221 | 2225.2415 | 15 | 25.3135 | 20 | 430
375 | 1 | 0 | 39.5813 | 39.6273 | 39.5915 | 39.6122 | 39.5333 | 39.5906 | 39.5963 | 39.6054 | 37.9136 | 30.8017 | 30.6743 | 53.3529 | 53.309 | 49.6848 | 49.7793 | 22.4529 | 11117.4029 | 49.5251 | 49.4405 | 46.8975 | 2216.7167 | 32.9961 | 39.5842 | 39.5849 | 39.5409 | 39.5693 | 30.7326 | 49.655 | 32.9 | 49.4557 | 53.3017 | 4.4884 | 3.0821 | 22.8442 | 17.8358 | 2348.9328 | 3212.2754 | 7.9905 | 8.1078 | 14.3339 | 3157.4148 | 41.8221 | 2225.2415 | 15 | 25.3135 | 27.1678 | 430
435 | 1 | 0 | 40.0535 | 40.1063 | 40.0854 | 40.099 | 40.0009 | 40.0798 | 40.0419 | 40.0749 | 38.2735 | 31.7857 | 31.6722 | 61.9598 | 62.0153 | 57.5516 | 57.6672 | 21.5335 | 10360.4755 | 56.4688 | 56.4621 | 53.2154 | 2217.5787 | 34.5093 | 40.0597 | 40.0826 | 40.0285 | 40.0562 | 31.7211 | 57.5419 | 34.4142 | 56.4476 | 61.9459 | 5.2224 | 3.6567 | 30.0211 | 23.4099 | 2621.6241 | 3353.1317 | 8.7447 | 8.8484 | 14.3339 | 3157.4148 | 41.7923 | 2225.3466 | 15 | 25 | 25 | 490
435 | 1 | 0 | 40.0535 | 40.1063 | 40.0854 | 40.099 | 40.0009 | 40.0798 | 40.0444 | 40.0749 | 38.2791 | 31.802 | 31.6852 | 61.9695 | 62.0115 | 57.5371 | 57.6553 | 21.5316 | 10360.4755 | 56.4649 | 56.4588 | 53.2104 | 2217.5811 | 34.5129 | 40.0572 | 40.0826 | 40.0285 | 40.0562 | 31.7285 | 57.5312 | 34.4182 | 56.436 | 61.9453 | 5.2265 | 3.6497 | 30.0179 | 23.4019 | 2621.4797 | 3353.1296 | 8.7447 | 8.8484 | 14.3339 | 3157.4148 | 41.7923 | 2225.3466 | 15 | 27 | 25 | 490
435 | 1 | 0 | 40.0535 | 40.1052 | 40.0854 | 40.099 | 40.0037 | 40.0872 | 40.0444 | 40.0749 | 38.2791 | 31.8059 | 31.6875 | 61.97 | 62.0162 | 57.5547 | 57.6391 | 21.5465 | 10360.4764 | 56.4672 | 56.4577 | 53.219 | 2217.5844 | 34.5296 | 40.0615 | 40.0826 | 40.0388 | 40.0562 | 31.7399 | 57.533 | 34.4466 | 56.4408 | 61.9481 | 5.2318 | 3.6401 | 30.0282 | 23.3914 | 2621.6165 | 3353.2879 | 8.7447 | 8.8484 | 14.3339 | 3157.4148 | 41.8018 | 2225.3474 | 15 | 27 | 31.5673 | 490
495 | 1 | 0 | 40.6924 | 40.7358 | 40.7293 | 40.7372 | 40.642 | 40.7188 | 40.7058 | 40.732 | 38.7637 | 33.0488 | 32.8766 | 70.8583 | 71.4216 | 65.8786 | 65.9856 | 20.8603 | 10360.4802 | 63.8964 | 63.8992 | 59.962 | 2218.5262 | 36.3342 | 40.6847 | 40.7264 | 40.6823 | 40.7116 | 32.9602 | 65.8843 | 36.3062 | 63.8715 | 71.1076 | 6.0616 | 4.3246 | 37.2329 | 29.0363 | 2773.1431 | 3489.4415 | 9.5802 | 9.6186 | 14.3339 | 3157.4148 | 41.6412 | 2225.3098 | 15 | 27 | 30 | 515
495 | 1 | 0 | 40.6954 | 40.7389 | 40.7293 | 40.7372 | 40.642 | 40.7188 | 40.7058 | 40.732 | 38.7637 | 33.0475 | 32.8798 | 70.8768 | 71.4321 | 65.88 | 65.9975 | 20.8632 | 10561.2043 | 63.8998 | 63.9004 | 59.9678 | 2218.5254 | 36.3317 | 40.6863 | 40.727 | 40.6823 | 40.7098 | 32.9535 | 65.8895 | 36.3012 | 63.8763 | 71.1134 | 6.0612 | 4.3246 | 37.231 | 29.0327 | 2772.9117 | 3489.2552 | 9.5802 | 9.6186 | 14.3339 | 3157.4148 | 41.6412 | 2225.3098 | 15 | 27 | 30 | 515
495 | 1 | 0 | 40.6954 | 40.7407 | 40.7293 | 40.7372 | 40.6495 | 40.7188 | 40.7041 | 40.732 | 38.7655 | 33.0572 | 32.8886 | 71.0087 | 71.4452 | 65.9088 | 65.9821 | 20.8501 | 10561.2073 | 63.9055 | 63.9103 | 59.9744 | 2218.527 | 36.3178 | 40.6863 | 40.727 | 40.6823 | 40.7098 | 32.9655 | 65.8865 | 36.3015 | 63.8858 | 71.1757 | 6.0934 | 4.3267 | 37.2313 | 29.0579 | 2772.7906 | 3489.2399 | 9.5802 | 9.6186 | 14.3339 | 3157.4148 | 41.6412 | 2225.309 | 15 | 27 | 13.4319 | 515
525 | 1 | 0 | 40.862 | 40.9155 | 40.8677 | 40.8703 | 40.8401 | 40.9013 | 40.8698 | 40.8878 | 38.9814 | 30.4423 | 30.3592 | 43.9645 | 44.0193 | 41.3686 | 41.3525 | 24.7462 | 9934.0521 | 42.1118 | 41.9458 | 40.1349 | 2215.9056 | 31.9026 | 40.8679 | 40.8575 | 40.8428 | 40.8554 | 30.3881 | 41.2931 | 31.7844 | 41.9921 | 43.9455 | 3.5305 | 2.398 | 14.7344 | 11.4394 | 1936.4781 | 3021.1985 | 6.4769 | 6.5106 | 14.3339 | 3157.4148 | 42.1421 | 2225.2785 | 15 | 27 | 5 | 160
525 | 1 | 0 | 40.862 | 40.9155 | 40.8677 | 40.8703 | 40.8401 | 40.9013 | 40.8655 | 40.8878 | 38.9814 | 30.4351 | 30.351 | 43.963 | 44.024 | 41.3665 | 41.3488 | 24.7437 | 9934.0521 | 42.1123 | 41.9404 | 40.1353 | 2215.9056 | 31.8986 | 40.8679 | 40.8575 | 40.8428 | 40.8554 | 30.3818 | 41.2942 | 31.7839 | 41.9921 | 43.9438 | 3.5305 | 2.4018 | 14.7332 | 11.4394 | 1936.4502 | 3021.0024 | 6.4769 | 6.5106 | 14.3339 | 3157.4148 | 42.1421 | 2225.2785 | 15 | 27 | 5 | 160
525 | 1 | 0 | 40.862 | 40.9155 | 40.8677 | 40.869 | 40.8401 | 40.9013 | 40.8655 | 40.8878 | 38.9814 | 30.4299 | 30.3465 | 43.9602 | 44.0098 | 41.3584 | 41.3416 | 24.7412 | 9934.0529 | 42.0979 | 41.9315 | 40.133 | 2215.9064 | 31.902 | 40.8679 | 40.8565 | 40.8428 | 40.8554 | 30.3778 | 41.2887 | 31.7839 | 41.99 | 43.94 | 3.5329 | 2.404 | 14.7407 | 11.446 | 1935.483 | 3020.6892 | 6.4769 | 6.5106 | 14.3339 | 3157.4148 | 42.1429 | 2225.2785 | 15 | 27 | 10.3615 | 160

## min
Time | Status (0-off 1-on) | Group (0-standalone 1-Group lead 2-Group follow) | TT01 | TT02 | TT31 | TT41 | TT61 | TT62 | TT51 | TT52 | TT45 | PT01 | PT02 | PT31 | PT41 | PT32 | PT42 | PT21 | PT11 | PT51 | PT52 | PT53 | PT61 | PT62 | TT01/TT02 | TT31/TT41 | TT61/TT62 | TT51/TT52 | PT01/PT02 | PT32/PT42 | PT61/PT62 | PT51/PT52 | Pump 31 Filter DP | Pump 41 Filter DP | Primary Filter 53 DP | Secondary DP (Supply - Return) | Primary DP (Supply - Return) | FT01 | FT61 | P31 Speed % | P41 Speed % | FCV61 Actual Flow% | FCV61 Actual Open% | Air Humidity | Air Temperature | Program version | Secondary Temperature Setpoint | Secondary DP Setpoint | Secondary Flow Setpoint
15 | 1 | 0 | 21.3 | 21.4 | 21.5 | 21.4 | 21.4 | 21.3 | 21.4 | 21.4 | 20.9 | 18.3 | 18.3 | 23.9 | 23.9 | 22.8 | 23.4 | 13.8 | 0 | 25.3 | 25.6 | 24.7 | 20.6 | 20.6 | 21.3 | 21.4 | 21.3 | 21.4 | 18.3 | 23.1 | 20.6 | 25.4 | 23.9 | 0.4 | 0.8 | 11.9 | 6.6 | 4.3 | 0 | 0 | 0 | 0 | 7.4 | 5.7 | 1.5 | 15 | 21 | 5 | 100
75 | 1 | 0 | 21.6 | 21.6 | 21.7 | 21.7 | 21.6 | 21.6 | 21.6 | 21.7 | 21.1 | 22.2 | 22.1 | 27.6 | 28.4 | 26.2 | 26.2 | 17 | 0 | 27.3 | 27.7 | 26.7 | 22.7 | 22.7 | 21.6 | 21.7 | 21.6 | 21.6 | 22.2 | 26.2 | 22.7 | 27.5 | 28 | 0.4 | 0.8 | 6.6 | 4.8 | 1099.7 | 694.3 | 5.6 | 5.6 | 0 | 9.9 | 5.7 | 1.4 | 15 | 21 | 5 | 160
75 | 1 | 0 | 21.6 | 21.6 | 21.7 | 21.7 | 21.6 | 21.6 | 21.6 | 21.7 | 21.1 | 22.2 | 22.1 | 27.6 | 28.4 | 26.2 | 26.2 | 17 | 0 | 27.3 | 27.7 | 26.7 | 22.7 | 22.7 | 21.6 | 21.7 | 21.6 | 21.6 | 22.2 | 26.2 | 22.7 | 27.5 | 28 | 0.4 | 0.8 | 6.6 | 4.8 | 1099.7 | 694.3 | 5.6 | 5.6 | 0 | 9.9 | 5.7 | 1.4 | 15 | 21 | 5 | 160
75 | 1 | 0 | 21.6 | 21.6 | 21.7 | 21.7 | 21.6 | 21.6 | 21.6 | 21.7 | 21.1 | 22.2 | 22.1 | 27.6 | 28.4 | 26.2 | 26.2 | 17 | 0 | 27.3 | 27.7 | 26.7 | 22.7 | 22.7 | 21.6 | 21.7 | 21.6 | 21.6 | 22.2 | 26.2 | 22.7 | 27.5 | 28 | 0.4 | 0.8 | 6.6 | 4.8 | 1096.8 | 694.3 | 5.6 | 5.6 | 0 | 9.9 | 5.7 | 1.4 | 15 | 21 | 10 | 160
135 | 1 | 0 | 21.8 | 21.8 | 21.9 | 21.9 | 21.8 | 21.8 | 21.8 | 21.9 | 21.2 | 21.9 | 21.8 | 30.4 | 30.7 | 28.4 | 28.4 | 17 | 0 | 29.1 | 29.5 | 28.3 | 22.7 | 22.8 | 21.8 | 21.9 | 21.8 | 21.9 | 21.9 | 28.4 | 22.7 | 29.3 | 30.7 | 0.5 | 0.9 | 9.2 | 6.8 | 1106.9 | 692.9 | 5.6 | 5.6 | 0 | 9.9 | 5.8 | 1.3 | 15 | 21 | 10 | 320
135 | 1 | 0 | 21.8 | 21.8 | 21.9 | 21.9 | 21.8 | 21.8 | 21.8 | 21.9 | 21.2 | 21.9 | 21.8 | 30.6 | 30.9 | 28.5 | 28.5 | 17 | 0 | 29.2 | 29.7 | 28.5 | 22.7 | 22.7 | 21.8 | 21.9 | 21.8 | 21.9 | 21.9 | 28.5 | 22.7 | 29.5 | 30.7 | 0.5 | 0.9 | 9.2 | 6.8 | 1106.9 | 692.9 | 5.6 | 5.6 | 0 | 9.9 | 5.8 | 1.3 | 15 | 22 | 10 | 320
135 | 1 | 0 | 21.8 | 21.8 | 21.9 | 21.9 | 21.8 | 21.8 | 21.8 | 21.9 | 21.2 | 21.9 | 21.8 | 30.6 | 30.9 | 28.5 | 28.5 | 17 | 0 | 29.2 | 29.7 | 28.5 | 22.7 | 22.7 | 21.8 | 21.9 | 21.8 | 21.9 | 21.9 | 28.5 | 22.7 | 29.5 | 30.7 | 0.5 | 0.9 | 9.2 | 6.8 | 1106.9 | 692.9 | 5.6 | 5.6 | 0 | 9.9 | 5.8 | 1.3 | 15 | 22 | 10 | 320
195 | 1 | 0 | 22.2 | 22.3 | 22.4 | 22.3 | 22.2 | 22.2 | 22.3 | 22.4 | 21.5 | 22.1 | 22 | 34.9 | 35.4 | 32.8 | 32.8 | 14.5 | 0 | 32.9 | 33.4 | 31.7 | 23.2 | 23.3 | 22.2 | 22.3 | 22.2 | 22.3 | 22.1 | 32.8 | 23.3 | 33.1 | 35.1 | 0.6 | 1.4 | 12.8 | 9.9 | 1384.3 | 833.8 | 5.6 | 5.6 | 0 | 9.9 | 5.8 | 1.3 | 15 | 22 | 25 | 480
195 | 1 | 0 | 22.2 | 22.3 | 22.4 | 22.3 | 22.2 | 22.2 | 22.3 | 22.4 | 21.5 | 22.1 | 22 | 34.9 | 35.4 | 32.8 | 32.8 | 14.6 | 0 | 32.9 | 33.4 | 31.7 | 23.2 | 23.3 | 22.2 | 22.3 | 22.2 | 22.3 | 22.1 | 32.8 | 23.3 | 33.1 | 35.1 | 0.6 | 1.4 | 12.8 | 9.9 | 1385.8 | 833.8 | 5.6 | 5.6 | 0 | 9.9 | 5.8 | 1.3 | 15 | 22 | 25 | 480
195 | 1 | 0 | 22.2 | 22.3 | 22.4 | 22.3 | 22.2 | 22.2 | 22.3 | 22.4 | 21.5 | 22.1 | 22 | 34.9 | 35.4 | 32.8 | 32.8 | 14.6 | 0 | 32.9 | 33.4 | 31.7 | 23.2 | 23.3 | 22.2 | 22.3 | 22.2 | 22.3 | 22.1 | 32.8 | 23.3 | 33.1 | 35.1 | 0.6 | 1.4 | 12.8 | 9.9 | 1385.8 | 833.8 | 5.6 | 5.6 | 0 | 9.9 | 5.8 | 1.3 | 15 | 23 | 25 | 480
255 | 1 | 0 | 23 | 23.1 | 23.2 | 23.1 | 23 | 23 | 23.1 | 23.2 | 21.9 | 22.3 | 22.3 | 34.6 | 35.5 | 32.4 | 32.5 | 13.4 | 0 | 32.8 | 33.2 | 31.7 | 23.2 | 23.3 | 23 | 23.1 | 23 | 23.1 | 22.3 | 32.5 | 23.3 | 33 | 35 | 0.4 | 1.3 | 12.7 | 9.7 | 1390.1 | 884.1 | 5.6 | 5.6 | 0 | 9.9 | 5.8 | 1.4 | 15 | 23 | 33 | 560
255 | 1 | 0 | 23 | 23.1 | 23.2 | 23.1 | 23 | 23 | 23.1 | 23.2 | 21.9 | 22.3 | 22.3 | 34.6 | 35.5 | 32.4 | 32.5 | 13.4 | 0 | 32.8 | 33.2 | 31.7 | 23.2 | 23.3 | 23 | 23.1 | 23 | 23.1 | 22.3 | 32.5 | 23.3 | 33 | 35 | 0.4 | 1.3 | 12.7 | 9.7 | 1390.1 | 884.1 | 5.6 | 5.6 | 0 | 9.9 | 5.8 | 1.4 | 15 | 23 | 33 | 560
255 | 1 | 0 | 23 | 23.1 | 23.2 | 23.1 | 23 | 23 | 23.1 | 23.2 | 21.9 | 22.3 | 22.3 | 34.6 | 35.5 | 32.4 | 32.5 | 13.4 | 0 | 32.8 | 33.2 | 31.7 | 23.2 | 23.3 | 23 | 23.1 | 23 | 23.1 | 22.3 | 32.5 | 23.3 | 33 | 35 | 2.3 | 1.3 | 12.7 | 9.7 | 1390.1 | 884.1 | 5.6 | 5.6 | 0 | 9.9 | 5.8 | 1.4 | 15 | 23 | 15 | 560
315 | 1 | 0 | 23.4 | 23.4 | 23.6 | 23.6 | 23.4 | 23.4 | 23.5 | 23.6 | 22.4 | 22 | 22 | 34.7 | 35.4 | 32.6 | 32.7 | 16.6 | 0 | 33.1 | 33.5 | 32 | 23.4 | 23.5 | 23.4 | 23.6 | 23.4 | 23.5 | 22.1 | 32.7 | 23.4 | 33.3 | 35.1 | 0.3 | 1.3 | 12.7 | 9.8 | 1229.1 | 731.7 | 5.6 | 5.6 | 0 | 9.9 | 5.7 | 1.6 | 15 | 23 | 15 | 380
315 | 1 | 0 | 23.4 | 23.4 | 23.6 | 23.6 | 23.4 | 23.4 | 23.5 | 23.6 | 22.4 | 22.2 | 22.1 | 34.8 | 35.3 | 32.6 | 32.8 | 16.6 | 0 | 33.1 | 33.4 | 31.9 | 23.4 | 23.5 | 23.4 | 23.6 | 23.4 | 23.5 | 22.1 | 32.7 | 23.4 | 33.3 | 35.1 | 0.3 | 1.3 | 12.7 | 9.8 | 1229.1 | 731.7 | 5.6 | 5.6 | 0 | 9.9 | 5.7 | 1.6 | 15 | 23 | 15 | 380
315 | 1 | 0 | 23.4 | 23.4 | 23.6 | 23.6 | 23.4 | 23.4 | 23.5 | 23.6 | 22.4 | 22.2 | 22.1 | 34.8 | 35.3 | 32.6 | 32.8 | 16.6 | 0 | 33.1 | 33.4 | 31.9 | 23.4 | 23.5 | 23.4 | 23.6 | 23.4 | 23.5 | 22.1 | 32.7 | 23.4 | 33.3 | 35.1 | 0.3 | 1.3 | 12.7 | 9.8 | 1229.1 | 731.7 | 5.6 | 5.6 | 0 | 9.9 | 5.7 | 1.6 | 15 | 24 | 15 | 380
375 | 1 | 0 | 23.8 | 23.8 | 23.9 | 23.9 | 23.8 | 23.8 | 23.8 | 23.9 | 22.7 | 22.2 | 22.2 | 35 | 35.7 | 32.8 | 32.9 | 15.8 | 0 | 33.1 | 33.5 | 31.9 | 23.4 | 23.4 | 23.8 | 23.9 | 23.8 | 23.9 | 22.2 | 32.8 | 23.4 | 33.3 | 35.3 | 0.1 | 1.3 | 12.8 | 9.9 | 1332.6 | 776.3 | 5.6 | 5.6 | 0 | 9.9 | 5.6 | 1.5 | 15 | 24 | 20 | 430
375 | 1 | 0 | 23.8 | 23.8 | 23.9 | 23.9 | 23.8 | 23.8 | 23.8 | 23.9 | 22.7 | 22.2 | 22.2 | 35 | 35.7 | 32.8 | 32.9 | 15.8 | 0 | 33.1 | 33.5 | 31.9 | 23.4 | 23.4 | 23.8 | 23.9 | 23.8 | 23.9 | 22.2 | 32.8 | 23.4 | 33.3 | 35.3 | 0.1 | 1.3 | 12.8 | 9.9 | 1332.6 | 776.3 | 5.6 | 5.6 | 0 | 9.9 | 5.6 | 1.5 | 15 | 24 | 20 | 430
375 | 1 | 0 | 23.8 | 23.8 | 23.9 | 23.9 | 23.8 | 23.8 | 23.8 | 23.9 | 22.7 | 22.2 | 22.2 | 35 | 35.7 | 32.8 | 32.9 | 15.8 | 0 | 33.1 | 33.5 | 31.9 | 23.4 | 23.4 | 23.8 | 23.9 | 23.8 | 23.9 | 22.2 | 32.8 | 23.4 | 33.3 | 35.3 | 0.1 | 1.3 | 12.8 | 9.9 | 1332.6 | 776.3 | 5.6 | 5.6 | 0 | 9.9 | 5.6 | 1.5 | 15 | 24 | 20 | 430
435 | 1 | 0 | 24.3 | 24.3 | 24.4 | 24.4 | 24.3 | 24.3 | 24.4 | 24.4 | 23.1 | 22.3 | 22.3 | 34.7 | 35.8 | 32.8 | 32.8 | 15 | 0 | 33.1 | 33.5 | 31.9 | 23.4 | 23.4 | 24.3 | 24.4 | 24.3 | 24.4 | 22.3 | 32.8 | 23.4 | 33.3 | 35.2 | 0.3 | 1.4 | 12.8 | 9.9 | 1371.4 | 820.8 | 5.6 | 5.6 | 0 | 9.9 | 5.8 | 1.4 | 15 | 25 | 25 | 490
435 | 1 | 0 | 24.3 | 24.3 | 24.4 | 24.4 | 24.3 | 24.3 | 24.4 | 24.4 | 23.1 | 22.3 | 22.3 | 34.7 | 35.8 | 32.8 | 32.8 | 15 | 0 | 33.1 | 33.5 | 31.9 | 23.4 | 23.4 | 24.3 | 24.4 | 24.3 | 24.4 | 22.3 | 32.8 | 23.4 | 33.3 | 35.2 | 0.3 | 1.4 | 12.8 | 9.9 | 1371.4 | 820.8 | 5.6 | 5.6 | 0 | 9.9 | 5.8 | 1.4 | 15 | 27 | 25 | 490
435 | 1 | 0 | 24.3 | 24.3 | 24.4 | 24.4 | 24.3 | 24.3 | 24.4 | 24.4 | 23.1 | 22.3 | 22.3 | 34.7 | 35.8 | 32.8 | 32.8 | 14.9 | 0 | 33.1 | 33.5 | 31.9 | 23.4 | 23.4 | 24.3 | 24.4 | 24.3 | 24.4 | 22.3 | 32.8 | 23.4 | 33.3 | 35.2 | 0.3 | 1.4 | 12.8 | 9.9 | 1371.4 | 820.8 | 5.6 | 5.6 | 0 | 9.9 | 5.8 | 1.4 | 15 | 27 | 25 | 490
495 | 1 | 0 | 25 | 25.1 | 25.2 | 25.1 | 25 | 25 | 25.1 | 25.2 | 23.6 | 22.3 | 22.3 | 35.3 | 35.3 | 32.9 | 32.8 | 13.9 | 0 | 33.2 | 33.6 | 32 | 23.4 | 23.4 | 25 | 25.1 | 25 | 25.1 | 22.3 | 32.8 | 23.4 | 33.4 | 35.3 | 0.2 | 1.4 | 12.8 | 10 | 1380 | 852.4 | 5.6 | 5.6 | 0 | 9.9 | 5.7 | 1.3 | 15 | 27 | 30 | 515
495 | 1 | 0 | 25 | 25.1 | 25.2 | 25.1 | 25 | 25 | 25.1 | 25.2 | 23.6 | 22.3 | 22.3 | 35.3 | 35.3 | 32.9 | 32.8 | 13.9 | 0 | 33.2 | 33.6 | 32 | 23.4 | 23.4 | 25 | 25.1 | 25 | 25.1 | 22.3 | 32.8 | 23.4 | 33.4 | 35.3 | 0.2 | 1.4 | 12.8 | 10 | 1380 | 855.3 | 5.6 | 5.6 | 0 | 9.9 | 5.7 | 1.3 | 15 | 27 | 30 | 515
495 | 1 | 0 | 25 | 25.1 | 25.2 | 25.1 | 25 | 25 | 25.1 | 25.2 | 23.6 | 22.2 | 22.2 | 34.7 | 35.3 | 32.8 | 32.9 | 13.9 | 0 | 33.2 | 33.6 | 32 | 23.4 | 23.5 | 25 | 25.1 | 25 | 25.1 | 22.2 | 32.8 | 23.5 | 33.4 | 35 | 0.2 | 1.4 | 12.8 | 9.9 | 1380 | 855.3 | 5.6 | 5.6 | 0 | 9.9 | 5.7 | 1.3 | 15 | 27 | 5 | 515
525 | 1 | 0 | 25.2 | 25.2 | 25.3 | 25.3 | 25.2 | 25.2 | 25.2 | 25.3 | 23.9 | 22.4 | 22.4 | 30.6 | 30.6 | 28.6 | 28.7 | 17.4 | 0 | 29.4 | 29.8 | 28.6 | 23.2 | 23.3 | 25.2 | 25.3 | 25.2 | 25.3 | 22.4 | 28.6 | 23.2 | 29.6 | 30.6 | 0.1 | 1 | 8.8 | 6.4 | 1111.2 | 678.5 | 5.6 | 5.6 | 0 | 9.9 | 5.7 | 1.4 | 15 | 27 | 5 | 160
525 | 1 | 0 | 25.2 | 25.2 | 25.3 | 25.3 | 25.2 | 25.2 | 25.2 | 25.3 | 23.9 | 22.4 | 22.4 | 30.6 | 30.6 | 28.6 | 28.7 | 17.4 | 0 | 29.4 | 29.8 | 28.6 | 23.2 | 23.3 | 25.2 | 25.3 | 25.2 | 25.3 | 22.4 | 28.6 | 23.2 | 29.6 | 30.6 | 0.1 | 1 | 8.8 | 6.4 | 1111.2 | 678.5 | 5.6 | 5.6 | 0 | 9.9 | 5.7 | 1.4 | 15 | 27 | 5 | 160
525 | 1 | 0 | 25.2 | 25.2 | 25.3 | 25.3 | 25.2 | 25.2 | 25.2 | 25.3 | 23.9 | 22.4 | 22.4 | 30.6 | 30.6 | 28.6 | 28.7 | 17.4 | 0 | 29.4 | 29.8 | 28.6 | 23.2 | 23.3 | 25.2 | 25.3 | 25.2 | 25.3 | 22.4 | 28.6 | 23.2 | 29.6 | 30.6 | 0.1 | 1 | 8.8 | 6.4 | 1111.2 | 678.5 | 5.6 | 5.6 | 0 | 9.9 | 5.7 | 1.4 | 15 | 27 | 0 | 160

## max
Time | Status (0-off 1-on) | Group (0-standalone 1-Group lead 2-Group follow) | TT01 | TT02 | TT31 | TT41 | TT61 | TT62 | TT51 | TT52 | TT45 | PT01 | PT02 | PT31 | PT41 | PT32 | PT42 | PT21 | PT11 | PT51 | PT52 | PT53 | PT61 | PT62 | TT01/TT02 | TT31/TT41 | TT61/TT62 | TT51/TT52 | PT01/PT02 | PT32/PT42 | PT61/PT62 | PT51/PT52 | Pump 31 Filter DP | Pump 41 Filter DP | Primary Filter 53 DP | Secondary DP (Supply - Return) | Primary DP (Supply - Return) | FT01 | FT61 | P31 Speed % | P41 Speed % | FCV61 Actual Flow% | FCV61 Actual Open% | Air Humidity | Air Temperature | Program version | Secondary Temperature Setpoint | Secondary DP Setpoint | Secondary Flow Setpoint
15 | 1 | 0 | 42.4 | 42.6 | 42.5 | 42.4 | 42.4 | 42.6 | 42.4 | 42.5 | 40.9 | 28.2 | 28.2 | 47.3 | 47.3 | 44.8 | 43.7 | 24.4 | 6553.5 | 44.2 | 44.2 | 42 | 6517.4 | 29.6 | 42.5 | 42.4 | 42.5 | 42.4 | 28.2 | 44.2 | 29.8 | 44.2 | 47.3 | 3.7 | 2.6 | 6553.5 | 6553.5 | 2343.1 | 6510.5 | 9.4 | 9.4 | 10 | 6551.2 | 49.3 | 6553 | 15 | 40 | 5 | 430
75 | 1 | 0 | 42.6 | 42.8 | 42.6 | 42.6 | 42.6 | 42.7 | 42.6 | 42.7 | 41.1 | 27.7 | 27.7 | 40.6 | 41 | 38.7 | 38.3 | 22.3 | 6553.5 | 39.4 | 39.1 | 37.3 | 6517.4 | 29 | 42.7 | 42.6 | 42.6 | 42.6 | 27.7 | 38.5 | 29.1 | 39.2 | 40.8 | 3.2 | 2.3 | 14 | 10.8 | 2343.1 | 6510.5 | 7.1 | 7.1 | 10 | 6551.2 | 49.4 | 6553 | 15 | 21 | 5 | 160
75 | 1 | 0 | 42.6 | 42.8 | 42.6 | 42.6 | 42.6 | 42.7 | 42.6 | 42.7 | 41.1 | 27.7 | 27.7 | 40.6 | 41 | 38.7 | 38.3 | 22.3 | 6553.5 | 39.4 | 39.1 | 37.3 | 6517.4 | 29 | 42.7 | 42.6 | 42.6 | 42.6 | 27.7 | 38.5 | 29.1 | 39.2 | 40.8 | 3.2 | 2.3 | 14 | 10.8 | 2343.1 | 6510.5 | 7.1 | 7.1 | 10 | 6551.2 | 49.4 | 6553 | 15 | 21 | 5 | 160
75 | 1 | 0 | 42.6 | 42.8 | 42.6 | 42.6 | 42.6 | 42.7 | 42.6 | 42.7 | 41.1 | 27.8 | 27.7 | 40.6 | 41 | 38.7 | 38.3 | 22.2 | 6553.5 | 39.3 | 39 | 37.3 | 6517.4 | 29 | 42.7 | 42.6 | 42.6 | 42.6 | 27.8 | 38.5 | 29.1 | 39.2 | 40.8 | 3.2 | 2.3 | 14 | 10.8 | 2343.1 | 6510.5 | 7.1 | 7.1 | 10 | 6551.2 | 49.4 | 6553 | 15 | 21 | 10 | 160
135 | 1 | 0 | 42.8 | 42.9 | 42.8 | 42.8 | 42.7 | 42.9 | 42.8 | 42.8 | 41.2 | 27.8 | 27.7 | 40.6 | 41 | 38.6 | 38.3 | 22.3 | 6553.5 | 39.3 | 39.1 | 37.2 | 6517.4 | 28.9 | 42.8 | 42.8 | 42.8 | 42.8 | 27.7 | 38.4 | 29.1 | 39.2 | 40.8 | 3.1 | 2.2 | 14 | 10.8 | 2343.1 | 6510.5 | 8.2 | 8.2 | 10 | 6551.2 | 49.4 | 6552.8 | 15 | 21 | 10 | 320
135 | 1 | 0 | 42.8 | 42.9 | 42.8 | 42.8 | 42.7 | 42.9 | 42.8 | 42.8 | 41.2 | 27.8 | 27.7 | 40.6 | 41 | 38.6 | 38.3 | 22.3 | 6553.5 | 39.3 | 39.1 | 37.2 | 6517.4 | 28.9 | 42.8 | 42.8 | 42.8 | 42.8 | 27.7 | 38.4 | 29.1 | 39.2 | 40.8 | 3.1 | 2.2 | 14 | 10.8 | 2343.1 | 6510.5 | 8.2 | 8.2 | 10 | 6551.2 | 49.4 | 6552.8 | 15 | 22 | 10 | 320
135 | 1 | 0 | 42.8 | 42.9 | 42.8 | 42.8 | 42.7 | 42.9 | 42.8 | 42.8 | 41.2 | 27.8 | 27.7 | 40.6 | 41 | 38.6 | 38.3 | 22.3 | 6553.5 | 39.3 | 39.1 | 37.2 | 6517.4 | 28.9 | 42.8 | 42.8 | 42.8 | 42.8 | 27.7 | 38.4 | 29.1 | 39.2 | 40.8 | 3.1 | 2.2 | 14 | 10.8 | 2343.1 | 6510.5 | 8.2 | 8.2 | 10 | 6551.2 | 49.4 | 6552.8 | 15 | 22 | 25 | 320
195 | 1 | 0 | 43.1 | 43.3 | 43.2 | 43.2 | 43.1 | 43.3 | 43.2 | 43.2 | 41.5 | 29.6 | 29.6 | 55.3 | 55.7 | 51.6 | 51.5 | 20.2 | 6553.5 | 51.3 | 51.1 | 48.2 | 6517.4 | 31.9 | 43.2 | 43.2 | 43.2 | 43.2 | 29.6 | 51.5 | 32.2 | 51.2 | 55.5 | 4.4 | 3.3 | 25.3 | 20 | 2343.1 | 6510.5 | 9.6 | 10.1 | 10 | 6551.2 | 49.4 | 6552.8 | 15 | 22 | 25 | 480
195 | 1 | 0 | 43.1 | 43.3 | 43.2 | 43.2 | 43.1 | 43.3 | 43.2 | 43.2 | 41.5 | 29.6 | 29.6 | 55.3 | 55.7 | 51.6 | 51.5 | 20.2 | 6553.5 | 51.3 | 51.1 | 48.2 | 6517.4 | 31.9 | 43.2 | 43.2 | 43.2 | 43.2 | 29.6 | 51.5 | 32.2 | 51.2 | 55.5 | 4.4 | 3.3 | 25.2 | 20 | 2343.1 | 6510.5 | 9.6 | 10.1 | 10 | 6551.2 | 49.4 | 6552.8 | 15 | 23 | 25 | 480
195 | 1 | 0 | 43.1 | 43.3 | 43.2 | 43.2 | 43.1 | 43.3 | 43.2 | 43.2 | 41.5 | 29.6 | 29.6 | 55.3 | 55.7 | 51.6 | 51.5 | 20.2 | 6553.5 | 51.3 | 51.1 | 48.2 | 6517.4 | 31.9 | 43.2 | 43.2 | 43.2 | 43.2 | 29.6 | 51.5 | 32.2 | 51.2 | 55.5 | 4.4 | 3.3 | 25.2 | 20 | 2343.1 | 6510.5 | 9.6 | 10.1 | 10 | 6551.2 | 49.4 | 6552.8 | 15 | 23 | 33 | 480
255 | 1 | 0 | 43.8 | 44 | 43.9 | 43.9 | 43.8 | 44 | 43.9 | 43.9 | 41.9 | 31.4 | 31.4 | 66 | 66.4 | 61.8 | 61.6 | 19.1 | 6553.5 | 60.3 | 60 | 56.4 | 6517.4 | 34.3 | 43.9 | 43.9 | 43.9 | 43.9 | 31.4 | 61.7 | 34.7 | 60.1 | 66.2 | 5.3 | 4.2 | 33.1 | 26.1 | 2343.1 | 6510.5 | 9.6 | 10.1 | 10 | 6551.2 | 49.5 | 6552.7 | 15 | 23 | 33 | 560
255 | 1 | 0 | 43.8 | 44 | 43.9 | 43.9 | 43.8 | 44 | 43.9 | 43.9 | 41.9 | 31.4 | 31.4 | 66 | 66.4 | 61.8 | 61.6 | 19.1 | 6553.5 | 60.3 | 60 | 56.4 | 6517.4 | 34.3 | 43.9 | 43.9 | 43.9 | 43.9 | 31.4 | 61.7 | 34.7 | 60.1 | 66.2 | 5.3 | 4.2 | 33.1 | 26 | 2343.1 | 6510.5 | 9.6 | 10.1 | 10 | 6551.2 | 49.5 | 6552.7 | 15 | 23 | 33 | 560
255 | 1 | 0 | 43.8 | 44 | 43.9 | 43.9 | 43.8 | 44 | 43.9 | 43.9 | 41.9 | 31.4 | 31.4 | 66 | 66.4 | 61.8 | 61.6 | 19.1 | 6553.5 | 60.3 | 60 | 56.4 | 6517.4 | 34.3 | 43.9 | 43.9 | 43.9 | 43.9 | 31.4 | 61.7 | 34.7 | 60.1 | 66.2 | 5.3 | 4.2 | 33.1 | 26 | 2343.1 | 6510.5 | 9.6 | 10.1 | 10 | 6551.2 | 49.5 | 6552.7 | 15 | 23 | 15 | 560
315 | 1 | 0 | 44.2 | 44.4 | 44.3 | 44.3 | 44.2 | 44.4 | 44.2 | 44.3 | 42.3 | 28.6 | 28.5 | 44.6 | 44.8 | 41.6 | 41.6 | 22.1 | 6553.5 | 42.4 | 42.1 | 40.1 | 6517.4 | 29.9 | 44.3 | 44.3 | 44.3 | 44.3 | 28.5 | 41.6 | 30.1 | 42.2 | 44.6 | 3.5 | 2.5 | 16.2 | 13.2 | 2343.1 | 6510.5 | 9.6 | 10 | 10 | 6551.2 | 49.5 | 6553 | 15 | 23 | 15 | 380
315 | 1 | 0 | 44.2 | 44.4 | 44.3 | 44.3 | 44.2 | 44.4 | 44.2 | 44.3 | 42.3 | 28.6 | 28.5 | 44.6 | 44.8 | 41.6 | 41.6 | 22.1 | 6553.5 | 42.4 | 42.1 | 40.1 | 6517.4 | 29.9 | 44.3 | 44.3 | 44.3 | 44.3 | 28.5 | 41.6 | 30.1 | 42.2 | 44.6 | 3.5 | 2.5 | 16.2 | 13.2 | 2343.1 | 6510.5 | 9.6 | 10 | 10 | 6551.2 | 49.5 | 6553 | 15 | 24 | 15 | 380
315 | 1 | 0 | 44.2 | 44.4 | 44.3 | 44.3 | 44.2 | 44.4 | 44.2 | 44.3 | 42.3 | 28.6 | 28.5 | 44.6 | 44.8 | 41.6 | 41.6 | 22.1 | 6553.5 | 42.4 | 42.1 | 40.1 | 6517.4 | 29.9 | 44.3 | 44.3 | 44.3 | 44.3 | 28.5 | 41.6 | 30.1 | 42.2 | 44.6 | 3.5 | 2.5 | 16.2 | 13.2 | 2343.1 | 6510.5 | 9.6 | 10 | 10 | 6551.2 | 49.5 | 6553 | 15 | 24 | 20 | 380
375 | 1 | 0 | 44.6 | 44.7 | 44.6 | 44.6 | 44.5 | 44.7 | 44.6 | 44.7 | 42.7 | 29.2 | 29.2 | 49.6 | 49.7 | 46.4 | 46.5 | 21.3 | 6553.5 | 46.7 | 46.4 | 43.9 | 6517.4 | 31.1 | 44.6 | 44.6 | 44.6 | 44.6 | 29.2 | 46.4 | 31.3 | 46.5 | 49.6 | 4.1 | 3 | 20.1 | 16.3 | 2343.1 | 6510.5 | 9.7 | 10.1 | 10 | 6551.2 | 49.5 | 6553 | 15 | 24 | 20 | 430
375 | 1 | 0 | 44.6 | 44.7 | 44.6 | 44.6 | 44.5 | 44.7 | 44.6 | 44.7 | 42.7 | 29.2 | 29.2 | 49.6 | 49.7 | 46.4 | 46.5 | 21.3 | 6553.5 | 46.7 | 46.4 | 43.9 | 6517.4 | 31.1 | 44.6 | 44.6 | 44.6 | 44.6 | 29.2 | 46.4 | 31.3 | 46.5 | 49.6 | 4.1 | 3 | 20.1 | 16.3 | 2343.1 | 6510.5 | 9.7 | 10.1 | 10 | 6551.2 | 49.5 | 6553 | 15 | 25 | 20 | 430
375 | 1 | 0 | 44.6 | 44.7 | 44.6 | 44.6 | 44.5 | 44.7 | 44.6 | 44.7 | 42.7 | 29.2 | 29.2 | 49.6 | 49.7 | 46.4 | 46.5 | 21.3 | 6553.5 | 46.7 | 46.4 | 43.9 | 6517.4 | 31.1 | 44.6 | 44.6 | 44.6 | 44.6 | 29.2 | 46.4 | 31.3 | 46.5 | 49.6 | 4.1 | 3 | 20.1 | 16.3 | 2343.1 | 6510.5 | 9.7 | 10.1 | 10 | 6551.2 | 49.5 | 6553 | 15 | 25 | 25 | 430
435 | 1 | 0 | 45 | 45.2 | 45.1 | 45.1 | 44.9 | 45.2 | 45 | 45.1 | 43 | 30.1 | 30 | 55.9 | 56.3 | 52.5 | 52.4 | 20.4 | 6553.5 | 51.9 | 51.8 | 48.8 | 6517.4 | 32.3 | 45.1 | 45.1 | 45.1 | 45.1 | 30 | 52.4 | 32.5 | 51.9 | 56.1 | 4.5 | 3.4 | 25.2 | 20.3 | 2343.1 | 6510.5 | 9.6 | 10.1 | 10 | 6551.2 | 49.5 | 6553.3 | 15 | 25 | 25 | 490
435 | 1 | 0 | 45 | 45.2 | 45.1 | 45.1 | 44.9 | 45.2 | 45 | 45.1 | 43 | 30.1 | 30 | 55.9 | 56.3 | 52.5 | 52.4 | 20.4 | 6553.5 | 51.9 | 51.8 | 48.8 | 6517.4 | 32.3 | 45.1 | 45.1 | 45.1 | 45.1 | 30 | 52.4 | 32.5 | 51.9 | 56.1 | 4.5 | 3.4 | 25.2 | 20.4 | 2343.1 | 6510.5 | 9.6 | 10.1 | 10 | 6551.2 | 49.5 | 6553.3 | 15 | 27 | 25 | 490
435 | 1 | 0 | 45 | 45.2 | 45.1 | 45.1 | 44.9 | 45.2 | 45 | 45.1 | 43 | 30.1 | 30 | 55.9 | 56.3 | 52.5 | 52.4 | 20.4 | 6553.5 | 51.9 | 51.8 | 48.8 | 6517.4 | 32.3 | 45.1 | 45.1 | 45.1 | 45.1 | 30 | 52.4 | 32.5 | 51.9 | 56.1 | 4.5 | 3.4 | 25.2 | 20.4 | 2343.1 | 6510.5 | 9.6 | 10.1 | 10 | 6551.2 | 49.5 | 6553.3 | 15 | 27 | 30 | 490
495 | 1 | 0 | 45.7 | 45.8 | 45.7 | 45.7 | 45.6 | 45.8 | 45.7 | 45.8 | 43.5 | 31.1 | 30.9 | 62.5 | 63.1 | 58.4 | 58.3 | 19.6 | 6553.5 | 57.4 | 57.2 | 53.9 | 6517.4 | 33.9 | 45.7 | 45.7 | 45.7 | 45.7 | 31 | 58.3 | 34.2 | 57.3 | 62.6 | 5 | 4 | 30.2 | 24.3 | 2343.1 | 6510.5 | 9.7 | 10.1 | 10 | 6551.2 | 49.4 | 6553.2 | 15 | 27 | 30 | 515
495 | 1 | 0 | 45.7 | 45.8 | 45.7 | 45.7 | 45.6 | 45.8 | 45.7 | 45.8 | 43.5 | 31.1 | 30.9 | 62.5 | 63.1 | 58.4 | 58.3 | 19.6 | 6553.5 | 57.4 | 57.2 | 53.9 | 6517.4 | 33.9 | 45.7 | 45.7 | 45.7 | 45.7 | 31 | 58.3 | 34.2 | 57.3 | 62.6 | 5 | 4 | 30.2 | 24.3 | 2343.1 | 6510.5 | 9.7 | 10.1 | 10 | 6551.2 | 49.4 | 6553.2 | 15 | 27 | 30 | 515
495 | 1 | 0 | 45.7 | 45.8 | 45.7 | 45.7 | 45.6 | 45.8 | 45.7 | 45.8 | 43.5 | 31.1 | 30.9 | 62.5 | 63.1 | 58.4 | 58.3 | 19.6 | 6553.5 | 57.4 | 57.2 | 53.9 | 6517.4 | 33.9 | 45.7 | 45.7 | 45.7 | 45.7 | 31 | 58.3 | 34.2 | 57.3 | 62.6 | 5 | 4 | 30.2 | 24.3 | 2343.1 | 6510.5 | 9.7 | 10.1 | 10 | 6551.2 | 49.4 | 6553.2 | 15 | 27 | 30 | 515
525 | 1 | 0 | 45.8 | 45.9 | 45.8 | 45.8 | 45.8 | 45.9 | 45.8 | 45.9 | 43.7 | 28.5 | 28.4 | 41.2 | 41.7 | 39.2 | 38.9 | 22.9 | 6553.5 | 40 | 39.7 | 37.9 | 6517.4 | 29.6 | 45.8 | 45.8 | 45.8 | 45.8 | 28.5 | 39.1 | 29.8 | 39.9 | 41.5 | 3.2 | 2.4 | 14 | 10.7 | 2343.1 | 6510.5 | 8.2 | 8.3 | 10 | 6551.2 | 49.5 | 6553.1 | 15 | 27 | 5 | 160
525 | 1 | 0 | 45.8 | 45.9 | 45.8 | 45.8 | 45.8 | 45.9 | 45.8 | 45.9 | 43.7 | 28.5 | 28.4 | 41.2 | 41.7 | 39.2 | 38.9 | 22.9 | 6553.5 | 40 | 39.7 | 37.9 | 6517.4 | 29.6 | 45.8 | 45.8 | 45.8 | 45.8 | 28.5 | 39.1 | 29.8 | 39.9 | 41.5 | 3.2 | 2.4 | 14 | 10.7 | 2343.1 | 6510.5 | 8.2 | 8.3 | 10 | 6551.2 | 49.5 | 6553.1 | 15 | 27 | 5 | 160
525 | 1 | 0 | 45.8 | 45.9 | 45.8 | 45.8 | 45.8 | 45.9 | 45.8 | 45.9 | 43.7 | 28.5 | 28.4 | 41.2 | 41.7 | 39.2 | 38.9 | 22.9 | 6553.5 | 40 | 39.7 | 37.9 | 6517.4 | 29.6 | 45.8 | 45.8 | 45.8 | 45.8 | 28.5 | 39.1 | 29.8 | 39.9 | 41.5 | 3.2 | 2.4 | 14 | 10.7 | 2343.1 | 6510.5 | 8.2 | 8.3 | 10 | 6551.2 | 49.5 | 6553.1 | 15 | 27 | 5 | 160